Job:

# Power Vent

# For RP2100™
Pool & Spa Heaters

Models 185 - 405

Engineer:

Contractor:

Prepared By: 	     		Date:

Versatile

Suitable for use with hydronic heating boilers
and hot water heaters

Permits sidewall venting

Allows use of vent pipe as small as 4" in diameter

Efficient

Maintains thermal efficiency of 82% on all 
appliance sizes

Multi-Position Capability

90° elbow can be rotated to align fan discharge
with vent pipe and reduce the number of 
fittings required

# Features

- Induced draft

- Plenum sized for appliance capacity

- Air flow proving switch, mounted and wired

- Fan motor relay, mounted and wired

- 230/115 Volt, 60 Hertz, 1.95/1.0 Amp, 130 CFM Max., 3200 RPM motor; Factory-wired for 230 Volt

- 90° elbow can be used as a termination cap for horizontal venting

- Heavy-duty galvanized steel cabinet

- Polytuf powder coat finish

- Indoor/Outdoor construction

- Easy installation

- Limited one-year warranty

- Shipped loose for field mounting

#### Power Vent

#### For RP2100 Models 185 - 405	Model

| RP2100 Model | Part Number | Dimensions (in.) |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | A | B | C | D |
| 185 | 008086 | 18-1/8 | 12-3/8 | 7-7/8 | 4-1/4 |
| 265 | 008086 | 18-1/8 | 12-3/8 | 7-7/8 | 4-1/4 |
| 335 | 008087 | 17-1/2 | 15-3/4 | 7-5/8 | 6 |
| 405 | 008087 | 17-1/2 | 15-3/4 | 7-5/8 | 6 |

NOTES:

- All units can exhaust flue gases at:

Horizontal

Up to 40 ft. of equivalent length vent pipe

90° elbow = 10 ft. equivalent length
45° elbow = 5 ft. equivalent length

Vertical

Up to 40 ft. straight vertical venting

For vents above 40 ft., a barometric damper is required.

2.	Vent pipe must meet Category III appliance venting requirements.

3.	Vent pipe sizes are based 300°F nominal flue temperature and sea-level operation. For installation under other conditions, please consult the factory.

Raypak, Inc.  2151 Eastman Avenue, Oxnard, CA  93030  (805) 278-5300  Fax (800) 872-9725  www.raypak.com

Raypak Canada Ltd.  2805 Slough St., Mississauga, Ontario, Canada L4T 1G2  (905) 677-7999  Fax (905) 677-8036  www.raypakcanada.com

Raypak Australia Pty. Ltd.  7 Geddes Street, Mulgrave, Victoria, Australia 3170  (6139) 560-4944  Fax (6139) 560-4974  www.raypak.com.au