Job:

# Hi Delta® - Type P

## Commercial Pool Heaters Models 1532B-2342B

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

Patent No. 7,044,124

Sealed Combustion Chamber

100% Factory Fire Tested

Efficiency: 85%

Minimum Non-condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-year Thermal Shock Warranty

Limited Five-year Heat Exchanger Warranty

Full Safety Diagnostics with Fault History

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-assisted

Standard “H” Bypass Shown

Proudly Assembled in the USA

Non-ferrous Bypass

Patented Burner Security Blanket

#### Heat Exchanger

- Brass Headers

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Cupro-Nickel Finned Tubing

- ASME Steel Tube Sheet

- Silicone High-Temp O-Rings

- 125 PSIG ASME Pressure Relief Valve

- Temperature and Pressure Gauge

- Water Connections

Left – Standard

Right – Option A-6

- Bronze Pump, 120V, 60Hz

- Non-ferrous Pool Bypass

#### Controls

- 120V, 60Hz, 1 Power Supply

- 120/24V 60Hz Transformer

- 100% Shut-off/Lockout

- Hot Surface Ignition Systems (2)

- Remote Flame Sensors (2)

- High Limit Control, Auto Reset

- On/Off Power Switch

- Manual Shut-off, Front-mounted

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switches

- Economaster Pump Time Delay

- Poolstat

- Diagnostic Panel with LCD Display

- 2 Lines, 20 Characters

#### Gas Train

- Combination Valves

- On/Off Firing

- Low Gas Pressure Switch, Manual

- Fuel

Natural Gas (Only on 2002B)

Propane Gas

- Design Certified ANSI Z21.56/
CSA 4.7

#### Burner

- Ultra-low NOx:
Less than 20 PPM

#### Construction

- Indoor/Outdoor Construction

- Enclosed Front Controls

- CSA Low Lead Certified ≤ .25% Lead

#### Venting

- Vent Location

Top – Standard

Rear – Option D-14

- Vent Termination Cap

Outdoor – Option D-11

Indoor, Horizontal – 
Option D-15

Indoor, Vertical (by others)

- Combustion Air

In-Line Filter Kit (TruSeal 
only) – Option D-17

#### Air Intake Elbow – 
Option D-16

#### Options

B-26	2-Stage Digital

B-21	4-Stage Digital

B-__	TempTracker Mod+ (Up to 16 Boilers)

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

Right Side

Left Side (Model 1802B   	Only)

F-10	Low Water Cut-off, Remote Probe

P-__	Cold Water Run System

(See Page 3)

S-2	Dual High Gas Pressure Switches, Manual Reset

X-1	SureRack® Kit*

X-2	SureRack Kit  	Above Grade Add-on (used with X-1)*

#### Regulatory Agency Requirements

G-1	CSD-1

*Lower unit requires manifold modification

#### Hi Delta – Type P

#### Models 1532B-2342B (H-Bypass Option)	Model

| Model | Max. Flow |  |  |
| --- | --- | --- | --- |
|  | GPM | ∆P (ft) | ∆T |
| P 1532B | 132 | 16.5 | 20 |
| P 1802B | 132 | 18.3 | 23 |
| P 2002B | 132 | 19.0 | 26 |
| P 2072B | 132 | 19.0 | 27 |
| P 2342B | 132 | 21.4 | 30 |

| Model |  | MBTUH |  |  |  | A Width |  | K |  | W |  | Amp Draw |  |  |  | Pump HP |  | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input |  | Output |  |  |  |  |  |  |  | Heater |  | Pump |  |  |  |  |  |
| P 1532B |  | 1530 |  | 1301 |  | 79-7/8 |  | 12 |  | 24-3/8 |  | <12 |  | 11 |  | 3/4 |  | 1225 |
| P 1802B |  | 1800 |  | 1530 |  | 91-1/8 |  | 14 |  | 28-1/8 |  | <12 |  | 11 |  | 3/4 |  | 1350 |
| P 2002B |  | 1999 |  | 1699 |  | 102-1/2 |  | 14 |  | 31-15/16 |  | <12 |  | 14** |  | 1 |  | 1450 |
| P 2072B |  | 2070 |  | 1760 |  | 102-1/2 |  | 14 |  | 31-15/16 |  | <12 |  | 14** |  | 1 |  | 1450 |
| P 2342B |  | 2340 |  | 1989 |  | 113-7/8 |  | 16 |  | 35-11/16 |  | <12 |  | 21** |  | 1-1/2 |  | 1520 |

Dimensions are in inches.

Ratings shown are for elevations up to 4,500 feet and for natural or propane gas.

For installation at elevations over 4,500 feet, please contact manufacturer.

** Requires separate circuit breaker

#### Hi Delta – Type P

#### Models 1532B-2342B (Cold Water Run Option)	Model

| Model | Max. Flow |  |  |
| --- | --- | --- | --- |
|  | GPM | ∆P (ft) | ∆T |
| P 1532B | 132 | 16.5 | 20 |
| P 1802B | 132 | 18.3 | 23 |
| P 2002B | 132 | 19.0 | 26 |
| P 2072B | 132 | 19.0 | 27 |
| P 2342B | 132 | 21.4 | 30 |

| Model |  | MBTUH |  |  |  | A Width |  | K |  | W |  | Amp Draw |  |  |  | Pump HP |  | Injector Pump HP |  | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Input |  | Output |  |  |  |  |  |  |  | Heater |  | Pump |  |  |  |  |  |  |
| P 1532B | 1530 |  | 1301 |  | 79-7/8 |  | 12 |  | 24-3/8 |  | <12 |  | 12 |  | 3/4 |  | 1/3 |  | 1225 |  |
| P 1802B | 1800 |  | 1530 |  | 91-1/8 |  | 14 |  | 28-1/8 |  | <12 |  | 12 |  | 3/4 |  | 1/3 * |  | 1460 |  |
| P 2002B | 1999 |  | 1699 |  | 102-1/2 |  | 14 |  | 31-15/16 |  | <12 |  | 14 |  | 1** |  | 3/4 * |  | 1560 |  |
| P 2072B | 2070 |  | 1760 |  | 102-1/2 |  | 14 |  | 31-15/16 |  | <12 |  | 14 |  | 1** |  | 3/4 * |  | 1560 |  |
| P 2342B | 2340 |  | 1989 |  | 113-7/8 |  | 16 |  | 35-11/16 |  | <12 |  | 21 |  | 1** |  | 3/4 * |  | 1620 |  |

Dimensions are in inches.

Ratings shown are for elevations up to 4,500 feet and for natural or propane gas.

For installation at elevations over 4,500 feet, please contact manufacturer.

*Separate 120 VAC or 240 VAC 1Ø power required for Cold Water Run option

** Requires separate circuit breaker

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com