# MVB® - Type P

## Pool Heaters
Models 504A-2004A

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- 83-83.3% Thermal Efficiency at Full Rate

- 100% Factory Fire-Tested

- VERSA IC® Integrated Controller with 7” Color Touchscreen Display

- Raymote™ remote connectivity provided standard

- On/Off Operation

- Full Safety Diagnostics with History

- Status Display Lights

- Cascade up to 4 Heaters – No External Sequencer Required

- CSA Low Lead Certified ≤ .25% Lead

- Maximum Outlet Water Temperature: 180°F

- Maximum Pool Setpoint 106°F (104°F Default)

Proudly Assembled in the USA

Minimum Inlet Water Temperature: 105°F

- Limited Five-Year Primary Heat Exchanger Warranty

- Ultra Low NOx, Less Than 20 PPM

#### Heat Exchanger

Bronze Headers

ASME HLW Stamped; 160 PSIG MAWP

National Board Listed

Cupronickel Fin Tubing

ASME Powder-Coated Tube Sheet

Silicone High-Temp O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

Manual Air Bleed

Temperature and Pressure Gauge,
Shipped Loose

Four pass primary heat exchanger

Stainless Steel Evaporator Plate

Heater Pump: Bronze, 120V, 1, 60Hz

#### Control

120V, 60Hz, 1Ø, Power Supply

120/24V 60Hz Transformer

VERSA IC® built-in controller

7” color HD touchscreen display

Raymote™ Wi-Fi remote connectivity

Ignition Module

3-Try – Standard

C-6  Single-Try – Optional

Remote Flame Sensor

High Limit Fixed Manual 180ºF

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Freeze Protection

Pump Switch

Alarm Dry Contact

Pump Time Delay

Blocked Condensate Switch

Water Temperature Sensors (4)

Cold Water Protection

- Cold Water Run

- H-Bypass

Modbus RTU BMS Port

B-85   BMS Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

B-86   BMS Gateway – LonWorks

#### Burner

Hot Surface Ignition (HSI)

Radially-Fired Knitted Burner

#### Gas Train

Fuel

Natural Gas

Propane (minimum grade HD-5)

Zero Governor Regulator

Dual-Seat Combination Valve

Electronic Firing Mode (P)

#### Construction

Indoor/Outdoor Construction

Front Controls Enclosed

PolyTuf Powder Coat Finish

Rear Connections (Water, Gas, Vent, Electrical, Comb. Air, Cond. Drain)

Combustion Air Filter – Shipped Loose

Design Certified ANSI Z21.56/CSA 4.3

Front Connection Low Voltage Wiring

CSA Low Lead Certified ≤ .25% Lead

#### Venting

Vent Termination Cap

Outdoor or Indoor, Vertical – 
Option D-11

Indoor, Horizontal – Option D-15

- Combustion Air

In-Line Filter Kit – Option D-17

Air Intake Elbow – Option D-16

- Extractor – Optional, Cat II

By others

Not required

#### Options

F-10	Low Water Cut-Off, Remote Probe

I-3	High Limit, Auto Reset, 
Adj., 40-180F

I-6	High Limit, Manual Reset, Adj., 100-200F

S-1	Low Gas Pressure Switch, 
Manual Reset

S-2	High Gas Pressure Switch, Manual Reset

Z-12	Condensate Treatment Kit

#### Additional Options or Accessories

Raypak, Inc.  2151 Eastman Avenue, Oxnard, CA  93030  (805) 278-5300  Fax (800) 872-9725  www.raypak.com

MVB® – Type P

Models 504A-2004A	Model

| With H-Bypass |  |  |  |
| --- | --- | --- | --- |
| Model | Pump |  |  |
|  | Model | HP | Amps |
| P-504A | 1611 | 1/4 | 6 |
| P-754A | 1611 | 1/4 | 6 |
| P-1104A | 1630 | 1/2 | 7 |
| P-1504A | 1634 | 1 | 14 |
| P-2004A | 1636 | 1-1/2 | 22 |

*Current draw is for pump only

(Supply breaker must have delayed trip)

CLEARANCES

|  | Certified Minimum | Recomm. Service |
| --- | --- | --- |
| Front | 24” | 24” |
| Rear | 12” | 24” |
| Right | 1” | – |
| Left | 1” | – |
| Top | 0” | 10” |
| Floor | 0” | – |
| Vent | 1” | – |

Shown without H-Bypass or Cold Water Run options

| Model | MBTUH |  |  | Dimensions (in.) |  |  |  |  |  |  |  |  |  |  |  |  | Ship Weight (Lbs.) |  | Foot- print (Ft2) |  | Amps** |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | B | D | E | F | G* | H | K | L | M | N | P | R | V |  |  |  |  |  |  |
|  | Input | Output | Height |  |  |  | NPT | NPT | Flue Ø |  |  | C/A Ø |  |  |  |  |  |  |  |  |  |
| P-504A | 500 | 415 | 43 | 30 | 35 | 23-3/4 | 1 | 2 | 8 | 13-3/4 | 14-1/8 | 6 | 36 | 8 | 2 | 600 |  | 5.4 |  | 12 |  |
| P-754A | 750 | 623 | 49 | 36 | 41 | 29-3/4 | 1 | 2 | 10 | 13-1/2 | 16 | 6 | 42 | 8 | 2 | 660 |  | 5.4 |  | 12 |  |
| P-1104A | 1100 | 916 | 55 | 43 | 47 | 35-3/4 | 1-1/4 | 2-1/2 | 10 | 13-1/2 | 16 | 6 | 49 | 8 | 2 | 720 |  | 5.4 |  | 12 |  |
| P-1504A | 1500 | 1250 | 61 | 50 | 53 | 41-3/4 | 1-1/4 | 2-1/2 | 12 | 13-3/4 | 18-1/8 | 8 | 53 | 8 | 2 | 780 |  | 5.4 |  | 12 |  |
| P-2004A | 1900 | 1583 | 75 | 61 | 65 | 53-3/4 | 2 | 2-1/2 | 14 | 13-1/2 | 20-1/8 | 8 | 69 | 9 | 5 | 940 |  | 5.4 |  | 18 |  |

| - Ratings shown are for elevations up to 4,500 feet. For installations at elevations above 4,500 feet, please consult the factory for additional instructions. No hardware changes requires below 10,000 feet. * For Natural Gas. For Propane, all sizes are 1” NPT. **Current draw is for heater only. (Supply breaker must have delayed trip.) - For direct vent applications, contact the factory about relocating the pump. |  |
| --- | --- |

| Model | RATES OF FLOW |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20°F ΔT |  | Minimum Flow |  |  | Maximum Flow |  |  |
|  | GPM | ΔP (ft.) | GPM | ΔP (ft.) | ΔT (°F) | GPM | ΔP (ft.) | ΔT (°F) |
| P-504A | N/A | N/A | 65 | 5.5 | 13 | 100 | 11.3 | 9 |
| P-754A | 65 | 6.4 | 65 | 6.4 | 20 | 100 | 13.8 | 13 |
| P-1104A | 94 | 13.6 | 85 | 11.5 | 22 | 113 | 18.6 | 17 |
| P-1504A | N/A | N/A | 102 | 18.7 | 25 | 113 | 22.2 | 23 |
| P-2004A | N/A | N/A | 102 | 22.7 | 32 | 113 | 27.2 | 29 |