# XTherm® - Type P

## Pool Heaters
Models 1005A-2005A

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- 97% Thermal Efficiency at Full Rate

- 100% Factory Fire Tested

- VERSA IC® Controller with 7” color touchscreen display

- Raymote™ remote connectivity provided standard

- Maximum Outlet Water Temperature Setpoint: 104°F

- Minimum Acceptable Inlet Water Temperature: 50°F

- CPVC Water Manifold

- Full Safety Diagnostics with History

- Status Display Lights

- Cascade up to 4 heaters – No external sequencer needed

- Limited Twenty-Five-Year Thermal Shock Warranty

Proudly Made in the USA

Limited Five-Year Primary Heat Exchanger Warranty

- Limited Ten-Year Secondary Heat Exchanger Warranty

- On/Off Operation

#### Heat Exchanger

Bronze Headers

ASME HLW Stamped; 75 PSIG MAWP

National Board Listed

Cupro Nickel Fin Tubing

ASME Powder-Coated Tube Sheet

Silicone High Temp O-Rings

ASME Pressure Relief Valve

75 PSIG – Standard

Manual Air Bleed Valve

T&P Gauge

Stainless Steel Condensing Heat Exchanger – U stamped

Stainless Steel Evaporator Plate

Boiler Pump: Bronze, 120V, 1, 60Hz

#### Control

120V, 60Hz, 1Ø, Power Supply

120/24V 60Hz Transformer

VERSA IC®

7” color HD touchscreen display

Raymote™ Wi-Fi remote connectivity

Ignition Module

3-Try – Standard

Single-Try – Option C-6

Remote Flame Sensor

High Limit Fixed Manual 180ºF

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Freeze Protection

Alarm Dry Contact

Pump Time Delay

Blocked Condensate Switch

Water Temperature Sensors (2 mounted, 2 loose with wells)

Cold Water Protection

#### Burner

Hot Surface Ignition (HSI)

Ultra-Low NOx: Less than 20 PPM

- (Natural Gas Only)

#### Gas Train

Fuel

Natural Gas

Propane (Grade HD-5)

Zero Governor Regulator

Dual-Seat Combination Valve

Electronic Firing Mode (P)

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

PolyTuf Powder Coat Finish

Rear Connections (Water, Gas, Vent, Electrical, Comb. Air, Cond. Drain)

Combustion Air Filter

Design Certified ANSI Z21.56/CSA 4.3

Front Connection Low Voltage Wiring

CSA Low Lead Certified ≤ .25% Lead

#### Venting

Vent Termination, Cat IV

Outdoor or Indoor, Vertical – 
Option D-11

Indoor, Horizontal – Option D-15

- Extractor – Optional, Cat II

By others

Not required

#### Options

D-32	PVC Vent Connection (Factory Mounted Only)

D-33	Polypropylene Vent Connection

F-10	Low Water Cut-Off, Remote Probe

I-5	High Limit, Manual Reset, Adj., 100-200F

S-1	Low Gas Pressure Switch, 
Manual Reset

S-2	High Gas Pressure Switch, Manual Reset

Z-12	Condensate Treatment Kit

#### Additional Options or Accessories

XTherm – Type P

Models 1005A-2005A	Model

NOTE:  Primary/Secondary plumbing is mandatory for proper operation.

CLEARANCES (in.)

|  | Front | Rear | Right | Left | Top | Floor | Vent |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Certified Minimum | 24 | 12 | 1 | 1 | 0 | 0 | 1 |
| Minimum Service | 24 | 36 | 24 | 1 | 10 | N/A | N/A |

| Model | Amp Draw |  |
| --- | --- | --- |
|  | Heater † | Accessories † |
| ☐ 1005A | 12** | 10 |
| ☐ 1505A | 12** | 14 |
| ☐ 2005A | 18** | 17 |

† Separate power connections are factory supplied and separate supply breakers must be field supplied.

** Current draw is for heater only (Supply breaker must have delayed trip).

| Model (P-) | MBTUH |  | Dimensions (in) |  |  |  |  |  |  |  |  |  |  |  | Ship Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | B Height | D | E | F | G* NPT | K Flue Ø | L | M | N C/A Ø | P | R | Y |  |
|  | Input | Output |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ☐ 1005A | 999 | 969 | 55-1/8 | 45 | 47-1/8 | 36-1/2 | 1-1/4 | 6 | 40-1/16 | 11-1/2 | 6 | 47-1/8 | 8-1/16 | 6-1/16 | 1065 |
| ☐ 1505A | 1500 | 1455 | 67-1/8 | 57 | 59-1/16 | 38-1/2 | 1-1/4 | 8 | 52-1/16 | 12-5/8 | 8 | 59-1/8 | 8-3/16 | 6-1/16 | 1234 |
| ☐ 2005A | 1999 | 1939 | 81-1/8 | 71 | 71-3/16 | 38-1/2 | 2 | 8 | 64-1/16 | 12-5/8 | 8 | 73-1/8 | 8-3/16 | 6-1/4 | 1461 |

| Note: Ratings shown are for elevations up to 2,000 feet. For installations at elevations above 2,000 feet, please consult the factory for additional instructions. | * For Propane Gas, all models are 1 NPT |
| --- | --- |