Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

85% Thermal Efficiency

100% Factory Fire Tested

Minimum Acceptable Inlet Water Temperature: 105°F

Full Safety Diagnostics with History

Footprint: Less Than 5-1/2 ft2

Limited Twenty-Year Thermal Shock Warranty

Limited Five-Year Heat Exchanger Warranty

On/Off Firing

Soft-Start Modulating Controller with LCD Display

Status Display Lights

#### Heat Exchanger

Bronze Headers

ASME HLW Stamped
160 PSIG Working Pressure

National Board Approved

Cupro Nickel Fin Tubing

ASME Powder-Coated Tube Sheet

Silicone High Temp O-Rings

ASME Pressure Relief Valve,

125 PSIG

Temperature and Pressure Gauge,
Shipped Loose

Stainless Steel Evaporator Plate

Bronze Pump (See table on pg. 2)

Drain Valves (2)

Air Vent

#### Control

120V, 60Hz, 1Ø, Power Supply

120/24V 60Hz Transformer

Ignition Module

3-Try – Standard

Single-Try – Option C-6

Hot Surface Ignition (HSI)

Remote Flame Sensor

High Limit, Auto Reset, Adj., 140(F

High Limit, Manual Reset, Fixed

Models 504-1504:  175(F

Models 2004:  200ºF

On/Off Power Switch

Flow Switch, Mtd

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Pump Switch

Pump Time Delay

Diagnostics Panel

#### Control (cont.)

On/Off Digital Poolstat, 106(F Max

Water Temperature Sensors (3) with Immersion Well

#### Burner

Ultra-Low NOx: Less than 20 PPM

#### Gas Train

Fuel

Natural Gas

Propane

Zero Governor Regulator

Dual-Seat Combination Valve

On/Off Firing with Soft-Start

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

PolyTuf Powder Coat Finish

Rear Connections (Water, Electrical, Gas, Vent, Combustion Air)

Design Certification

ANSI Z21.56/
CSA 4.7

CSA Low Lead Certified ≤ .25 Pb

#### Venting

Vent Termination Cap

Outdoor – Option D-11

Indoor, Horizontal – Option D-15

Indoor, Vertical (by others)

Combustion Air

In-Line Filter Kit – Option D-17

Air Intake Elbow – Option D-16

Extractor – Optional

By others

Not required

#### Temperature Controllers

B-26	TempTracker Digital Controller, 
Up to 2 Heaters

B-21 	TempTracker Digital Controller, 
Up to 4 Heaters

B-  	TempTracker Mod+ (Up to 16 Boilers)

#### Options

F-10	Low Water Cut-Off, Remote Probe

P-  	Cold Water Run

P-  	H-style Bypass, Non-Ferrous

S-1	Low Gas Pressure Switch, 
Manual Reset

S-2	High Gas Pressure Switch, Manual Reset

#### Regulatory Agency Requirements

MVB – Type P

Models 504-2004	Model

Shown without H-bypass or Cold Water Run options

| Model | MBTUH | Dimensions (in.) | Ship Weight (Lbs.) | Foot- print (Ft2) | Amps* |
| --- | --- | --- | --- | --- | --- |
|  |  | B | D | E | F | G | H | K | M | N | P | R | V |  |  |  |
|  | Input | Output | Height |  |  |  | NPT | NPT | Flue Ø |  | C/A Ø |  |  |  |  |  |  |
| P-504 | 500 | 420 | 43 | 30 | 35 | 23-3/4 | 1 | 2 | 8 | 14-1/8 | 6 | 36 | 8 | 2 | 600 | 5.4 | 12 |
| P-754 | 750 | 630 | 49 | 36 | 41 | 29-3/4 | 1 | 2 | 10 | 16 | 6 | 42 | 8 | 2 | 660 | 5.4 | 12 |
| P-1104 | 1100 | 935 | 55 | 43 | 47 | 35-3/4 | 1-1/4 | 2-1/2 | 10 | 16 | 6 | 49 | 8 | 2 | 720 | 5.4 | 12 |
| P-1504 | 1500 | 1275 | 61 | 50 | 53 | 41-3/4 | 1-1/4 | 2-1/2 | 12 | 18-1/8 | 8 | 53 | 8 | 2 | 780 | 5.4 | 12 |
| WHP-2004 | 1900 | 1615 | 75 | 61 | 65 | 53-3/4 | 2 | 2-1/2 | 14 | 20-1/8 | 8 | 69 | 9 | 5 | 940 | 5.4 | 18 |

| Ratings shown are for elevations up to 4,500 feet. For installations at elevations above 4,500 feet, please consult the factory for additional instructions. | * Current draw is for heater only. (Supply breaker must have delayed trip.) |
| --- | --- |

| Model | RATES OF FLOW |
| --- | --- |
|  | 20°F (T | Minimum Flow | Maximum Flow |
|  | GPM | (P (ft.) | GPM | (P (ft.) | (T (°F) | GPM | (P (ft.) | (T (°F) |
| P-504 | N/A | N/A | 65 | 5.5 | 13 | 100 | 11.3 | 9 |
| P-754 | 65 | 6.4 | 65 | 6.4 | 20 | 100 | 13.8 | 13 |
| P-1104 | 94 | 13.6 | 85 | 11.5 | 22 | 113 | 18.6 | 17 |
| P-1504 | N/A | N/A | 102 | 18.7 | 25 | 113 | 22.2 | 23 |
| WHP-2004 | N/A | N/A | 102 | 22.7 | 32 | 113 | 27.2 | 29 |

# Text boxes

# MVB® - Type P

## Pool Heaters
Models 504-2004

Pump included standard

Proudly Made in the USA

Raypak, Inc. ( 2151 Eastman Avenue, Oxnard, CA  93030 ( (805) 278-5300 ( Fax (800) 872-9725 ( www.raypak.com

CLEARANCES

|  | Certified Minimum | Recomm. Service |
| --- | --- | --- |
| Front | 24” | 24” |
| Rear | 12” | 24” |
| Right | 1” | – |
| Left | 1” | – |
| Top | 0” | 10” |
| Floor | 0” | – |
| Vent | 1” | – |

PUMP

| Model | Pump |
| --- | --- |
|  | Model | HP | Amps* |
| P-504 | 1611 | ¼ | 6 |
| P-754 | 1630 | ½ | 7 |
| P-1104 | 1630 | ½ | 7 |
| P-1504 | 1634 | 1 | 14 |
| WHP-2004 | 1636 | 1 ½ | 22 |

* Current draw is for pump only