Catalog No.:    6000.70

Effective:	09-15-16

Replaces:	NEW

XTHERM®, TYPE P - MODELS 2505-4005
SUGGESTED SPECIFICATIONS

Catalog No.:    6000.63B

Effective:	3-01-15

Replaces:	9-01-09

XTHERM®, TYPE P - MODELS 1005A-2005A
SUGGESTED SPECIFICATIONS

### WATER-TUBE POOL HEATERS

- GENERAL

SUMMARY

Section includes condensing, gas-fired copper finned-tube, gas domestic pool heaters

Specifier Note:  Use as needed

Related Sections

Building Services Piping – Division 22 10 00

Breeching, Chimneys, and Stacks (Venting) – Division 23 51 00

Electrical – Division 23 09 33

REFERENCES

ANSI Z21.56/CSA 4.7

ASME, Sections IV and VIII

2006 UMC, Section 1107.6

ANSI/ASHRAE 15-1994, Section 8.13.6

National Fuel Gas Code, ANSI Z223.1/NFPA 54

National Electrical Code, ANSI/NFPA 70

ASME CSD-1, 2012 (when required)

SUBMITTALS

Product data sheet (including dimensions, rated capacities, shipping weights, accessories)

Wiring diagram

Warranty information

Installation and operating instructions

QUALITY ASSURANCE

Regulatory Requirements

ANSI Z21.56/CSA 4.3

Local and national air quality regulations for low NOx (0-30 PPM NOx emissions) pool heaters

Certifications

CSA

ASME HLW Stamp and National Board Listed – Primary

ASME U Stamp and National Board Listed – Secondary

ISO 9001

WARRANTY

Limited one-year warranty from date of installation

Limited twenty-five-year thermal shock warranty

Limited five-year primary heat exchanger warranty

Limited ten-year secondary heat exchanger warranty

- PRODUCTS

MANUFACTURER

Raypak, Inc.

Contact: 2151 Eastman Ave., Oxnard, CA 93030; Telephone: (805) 278-5300; 
Fax: (800) 872-9725; Web site: www.raypak.com

Product: XTherm® condensing cupro-nickel finned-tube pool heater(s)

POOL HEATERS

General

The pool heater(s) shall be fired with              gas at a rated input of              BTU/hr.

The pool heater(s) shall be CSA tested and certified with a minimum thermal efficiency of 97 percent at full fire.

The pool heater(s) shall be ASME inspected and stamped and National Board registered for 160 PSIG maximum allowable working pressure and 170ºF maximum allowable temperature, complete with a Manufacturer's Data Report.

The pool heater(s) shall have a floor loading of 146 lbs. /square foot or less.

Primary Heat Exchanger

The primary heat exchanger shall be of a single-bank, vertical multi-pass design and shall completely enclose the combustion chamber for maximum efficiency. The tubes shall be set vertically and shall be rolled into a powder-coated, ASME pool heater quality, carbon steel tube sheet.

The primary heat exchanger shall be sealed to 160 PSIG rated bronze headers with silicone "O" rings, having a temperature rating over 500°F.

The low water volume primary heat exchanger shall be explosion-proof on the water side and shall carry a twenty-five-year warranty against thermal shock.

The headers shall be secured to the tube sheet by stud bolts with flange nuts to permit inspection and maintenance without removal of external piping connections. A heavy gauge stainless steel slotted primary heat exchanger wrap shall ensure proper combustion gas flow across the copper-finned tubes.

The pool heater(s) flue connection, combustion air opening, gas connection, water connections, condensate drain and electrical connections shall be located on the rear.

The primary heat exchanger shall have accessible pool heater drain valves with hose bibs to drain the water section of the primary heat exchanger.

Secondary Heat Exchanger

The secondary heat exchanger shall be a single-bank, multi-pass design constructed of stainless steel and bear the ASME U stamp.

The pool heater(s) shall be capable of operating at inlet water temperatures as low as 50°F.

Condensate Drain

The heater(s) will feature a condensate drain switch which will shut down the heater(s) if the condensate drain is blocked.

Burners

The combustion chamber shall be of the sealed combustion type employing the Raypak high temperature FeCrAloy woven mesh burner, mounted in a vertical orientation.

The burner must be capable of firing at both a complete blue flame with maximum gas and air input as well as firing infrared when gas and air are reduced. The burner must be capable of firing at 100% of rated input when supplied with 4.0” WC of inlet gas pressure, so as to maintain service under heavy demand conditions; no exceptions.

The burner shall use a combustion air blower to precisely control the fuel/air mixture for maximum efficiency. The combustion air blower shall operate for a pre-purge period before burner ignition and a post-purge period after burner operation to clear the combustion chamber.

Ignition System

The pool heater(s) shall be equipped with a 100 percent safety shutdown.

The ignition shall be Hot Surface Ignition type with full flame rectification by remote sensing separate from the ignition source, with a three-try-for-ignition sequence, to ensure consistent operation.

The igniter will be located to the side of the heat exchanger to protect the device from condensation during start-up.

The ignition control module shall include an LED that indicates 15 individual diagnostic flash codes.

An external viewing port shall be provided, permitting visual observation of burner operation.

Gas Train

The pool heater(s) shall have a firing/leak test valve and pressure test valve as required.

The pool heater(s) shall have dual-seated main gas valve.

Gas control trains shall have a redundant safety shut-off feature, main gas regulation, shut-off cock and plugged pressure tapping to meet the requirements of ANSI Z21.56/CSA 4.7.

Pool Heater Control

The following safety controls shall be provided:

High limit control with manual reset fixed 180°F.

Flow switch, mounted and wired.

PSIG ASME pressure relief valve, piped by the installer to an approved drain.

Temperature and pressure gauge.

The pool heater(s) shall be equipped with a VERSA IC® temperature controller with color touchscreen display that incorporates an adjustable energy-saving pump control relay and freeze protection, and is factory mounted and wired to improve system efficiency; three water sensors included (system sensor and supply-to-pool sensor are loose).

Firing Mode: Provide electronic modulating control of the gas input to the pool heater.

Pool Heater Diagnostics

Provide external LED panel displaying the following pool heater status/faults:

Power on – Green

Call for heat – Amber

Burner firing – Blue

Service – Red

      - Provide monitoring of all safeties, internal/external interlocks with fault display by a 7” in. Color Touchscreen Display:

        - System status

        - Ignition failure

        - Condensate blockage

        - Blower speed error

        - Low 24 VAC

        - Manual reset high limit

        - Auto reset high limit

        - Blocked vent

        - High gas pressure switch (standard)

        - Controller alarm

        - Flow switch

        - Sensor failure

        - Factory option

          - Inlet sensor (open or short)

          - Outlet sensor (open or short)

          - System sensor (open or short)

          - Air sensor (open or short)

          - Indirect DHW sensor (open or short)

          - Indirect DHW tank sensor (open or short)

          - Cold water protection sensor (open or short)

          - Internal control fault

          - ID card fault

          - Cascade communications error

Specifier Note: The remaining items in this section are options. Delete those that are not being specified.

          - Auto reset high limit (optional)

          - Low water cut-off (optional)

          - Low gas pressure switch (optional)

Provide ignition module indicating the following flash codes by LED signal and displayed on LCD display:

1 flash – low air pressure

2 flashes – flame in the combustion chamber w/o CFH

3 flashes – ignition lock-out (flame failure)

4 flashes – low hot surface igniter current

5 flashes – low 24VAC

6 flashes – vent temperature

7 flashes – hi-Limit

8 flashes – sensor fault

9 flashes – low gas pressure

10 flashes – water pressure

11 flashes – blower speed fault

12 flashes – low water cut-off

13 flashes – hi-temperature ΔT

14 flashes – Ft-Bus communications

15 flashes – general safety limit

Combustion Chamber: The combustion chamber wrapper shall be insulated to reduce standby radiation losses, reduce jacket losses and increase unit efficiency.

Cabinet

The corrosion-resistant galvanized-steel jackets shall be finished with a baked-on powder coat, which is suitable for outdoor installation, applied prior to assembly for complete coverage, and shall incorporate louvers in the outer panels to divert air past heated surfaces.

The pool heater(s), if located on a combustible floor, shall not require a separate combustible floor base.

The pool heater(s) shall connect both the combustion air and flue products through the back of the unit.

The heater shall have as standard an internal, combustion air filter rated to MERV 8 (>95% arrestance).

Pool Heater Pump – Heater equipped with factory-packaged pump system.

Cold Water Protection System

The heater(s) shall be configured with a cold water protection automatic proportional bypass system that ensures the primary heat exchanger will experience inlet temperatures in excess of 120°F in less than 7 minutes to avoid damaging condensation.

The cold water protection system shall be configured with an injection pump (shipped loose) and a proportional two-way valve that is controlled by a system-matched PID control that injects the correct amount of cold water directly into the heater loop to maintain the required minimum inlet temperature. The PID controller temperature sensor shall be located in the inlet header of the primary heat exchanger.

POOL Heater OPERATING CONTROLS

The pool heater(s) shall feature a digital controller, mounted and wired.

System water sensor and supply-to-pool sensor shall be shipped loose for field-installation by installing contractor. Inlet/Outlet sensors are factory-installed.

DIRECT VENT

The pool heater(s) shall meet safety standards for direct vent equipment as noted by the 2006 Uniform Mechanical Code, section 1107.6, and ASHRAE 15-1994, section 8.13.6.

SOURCE QUALITY CONTROL

The pool heater(s) shall be completely assembled, wired, and fire-tested prior to shipment from the factory.

The pool heater(s) shall be furnished with the sales order, ASME Manufacturer’s Data Report(s), inspection sheet, wiring diagram, rating plate and Installation and Operating Manual.

- EXECUTION

INSTALLATION

Must comply with:

Local, state, provincial, and national codes, laws, regulations and ordinances

National Fuel Gas Code, ANSI Z223.1/NFPA 54 – latest edition

National Electrical Code, ANSI/NFPA 70 – latest edition

Canada only: CAN/CGA B149 Installation Code and CSA C22.1 CEC Part I

Manufacturer’s installation instructions, including required service clearances and venting guidelines

Manufacturer’s representative to verify proper and complete installation.

START-UP

Shall be performed by Raypak factory-trained personnel.

Test during operation and adjust if necessary:

Safeties

Operating Controls

Static and full load gas supply pressure

Gas manifold and blower air pressure

Combustion analysis

Submit copy of start-up report to Architect and Engineer.

training

Provide factory-authorized service representative to train maintenance personnel on procedures and schedules related to start-up, shut-down, troubleshooting, servicing, and preventive maintenance.

Schedule training at least seven days in advance.

- END OF SECTION