# Hi Delta® - Type P

## Commercial Pool Heaters Models 502C-902C

# Hi Delta® - Type P

## Commercial Pool Heaters Models 502C-902C

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

- 100% Factory Fire Tested

- Thermal Efficiency: 83.1%

- Versa IC® Controller with LCD Display

- Maximum Setpoint: 106°F (104°F Default)

- Maximum Outlet Temperature: 160°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal-Shock Proof Heat Exchanger

- Limited Twenty-Year Thermal Shock Warranty

- Limited Five-Year Heat Exchanger Warranty

- Full Safety Diagnostics with Fault History

- PolyTuf Powder Coated Cabinet

- No Combustible Floor Shield Required

- Fan-Assisted

- Patented Burner Security Blanket

Proudly Assembled in the USA

Proudly Assembled in the USA

Ultra-Low NOx – SCAQMD 1146.2 Certified

- Cascade Up To 4 Heaters – No External Sequencer Needed

Standard Sparcomatic

Bypass Shown

Standard Sparcomatic

Bypass Shown

#### Heat Exchanger

Brass Headers

ASME Inspected and HLW Stamped
160 PSIG Working Pressure

National Board Approved

Cupro-Nickel Finned Tubing

ASME Steel Tube Sheet

Silicone High-Temp O-Rings

125 PSIG ASME Pressure Relief Valve

Temperature and Pressure Gauge

Water Connections

Left – Standard

A-6 – Right

Bronze Pump, 1/2 HP, 120V, 60Hz

Non-ferrous Pool Bypass Assembly

- with Automatic Control

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

Versa IC® Integrated Control

Cascade up to 4 Heaters

100% Shut-Off/Lockout

Hot Surface Ignition

Ignition Module

- 3-Try – Standard

- C-6 Single Try

Remote Flame Sensor

Fixed High Limit, Manual Reset 240°F

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Programmable Pump Time Delays

- Heater

- System

Enable/Disable

LCD Display; Status, Fault and Diagnostics

#### Controls – Cont.

Cold Water Protection Function

- CWR Variable-Speed Pump

- Default Sparcomatic Bypass

Modbus RTU BMS Port (Up to 115K Baud Rate, See Cat. 5000.73)

- B-85 – BMS Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

- B-86 – BMS Gateway - LonWorks

#### Gas Train

Combination Valves

On/Off Firing

Fuel

Natural Gas

Propane Gas (HD-5)

G–20 4” WC Nat. Supply

Design Certified ANZI Z21.56/
CSA 4.7

#### Burner

Ultra-low NOx:
Less than 20 PPM

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

PolyTuf Powder Coat Finish

CSA Low Lead Certified ≤ .25% Lead

#### Venting

Vent Location

Top – Standard

D – 14 Rear

Vent Termination Cap

D – 11 Outdoor

D – 15 Horizontal

Indoor, Vertical (by others)

Combustion Air

D – 17 In-Line Filter Kit (TruSeal only)

D – 16 Air Intake Elbow

#### Venting – Cont.

Extractor - Optional

By Others

Not Required

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

Left Side - Standard 
 Right Side - Optional

F-10	Low Water Cut-Off, 
Remote Probe

S-1	Low Gas Pressure Switch, Manual Reset

S-2		High Gas Pressure Switch, Manual Reset

X-1	SureRack® Kit (Lower Unit Requires Manifold Modification)

X-2	SureRack Add-On (Lower Unit Requires Manifold Modification)

Additional Options or Accessories

Multi-Heater Controllers

#### B-36	2 – 4 Heaters

#### B-37	5 – 10 Heaters

#### B-38	11 – 16 Heaters

#### B-39	EMS 4-20mA Remote Setpoint Module

#### B-62	BACnet MS/TP Interface

#### Hi Delta – Type P

#### Models 502C – 902C (“Sparcomatic’’ Bypass Option)	Model

| Rate of Heat Exchanger Flow and Pressure and Temperature Drop |  |  |  |
| --- | --- | --- | --- |
|  | GPM | ΔP (ft.) | ΔT (ºF) |
| 502C | 90 | 10.5 | 10 |
| 652C |  | 10.7 | 12 |
| 752C |  | 11.0 | 14 |
| 902C |  | 11.8 | 17 |

| Model | MBTUH |  | A Width | K | W | Amp Draw (w/ Pump) | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output 83.1% |  |  |  |  |  |
| 502C | 500 | 416 | 50 | 6 | 22 | 13 | 545 |
| 652C | 650 | 540 | 60-1/2 | 8 | 27-1/4 | 13 | 590 |
| 752C | 750 | 623 | 67-1/2 | 8 | 30-3/4 | 13 | 675 |
| 902C | 900 | 748 | 78 | 8 | 36 | 14 | 740 |

NOTES:	1. Dimensions are in inches.

2. Rates shown are for natural or propane gas, and elevations up to 4,500 feet.

For installation above 4,500 feet, please contact manufacturer.

#### Hi Delta – Type P

#### Models 502C – 902C (Cold Water Run Option)	Model

| Rate of Heat Exchanger Flow and Pressure and Temperature Drop |  |  |  |  |
| --- | --- | --- | --- | --- |
| Model | GPM | ΔP (ft.) | ΔT (ºF) | Injector Flow (GPM) |
| 502C | 90 | 10.5 | 10 | 22 |
| 652C |  | 10.7 | 12 | 28 |
| 752C |  | 11.0 | 14 | 32 |
| 902C |  | 11.8 | 17 | 38 |

| Model | MBTUH |  | A Width | K | W | Amp Draw Heater w/ Pump | Injector Pump HP | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output 83.1% |  |  |  |  |  |  |
| P 502C | 500 | 416 | 50 | 6 | 22 | 13 | 1/4 | 655 |
| P 652C | 650 | 540 | 60-1/2 | 8 | 27-1/4 | 13 |  | 755 |
| P 752C | 750 | 623 | 67-1/2 | 8 | 30-3/4 | 13 |  | 815 |
| P 902C | 900 | 748 | 78 | 8 | 36 | 14 |  | 905 |

NOTES:	1. Dimensions are in inches.

2. Rates shown are for natural or propane gas, and elevations up to 4,500 feet.

For installation above 4,500 feet, please contact manufacturer.

3. Separate 120 VAC or 240 VAC 1Ø power required for Cold Water Run Option.

Raypak, Inc. ▪ 2151 Eastman Avenue, Oxnard, CA 93030 ▪ (805) 278-5300 ▪ Fax (805) 872-9725 ▪ www.raypak.com

4. Injector pump ships loose for field installation at bypass inlet.