Job:

# D-2 Power Vent

## For Pool & Spa Heaters
Models 206-407

Engineer:

Contractor:

Prepared By: 	     		Date:

Versatile

- For use with pool and spa heaters

- Permits sidewall venting

- Allows use of vent pipe as small as 4 in. diameter

Efficient

- Maintains thermal efficiency of 82% on all 
heater sizes

Multi-Position Capability

- 90° elbow can be rotated to align fan discharge with vent pipe and reduce the number of fittings required

# Features

- Induced draft

- Vent (Category III) runs up to 100 ft. equivalent length

- Plenum sized for appliance capacity

- Air flow proving switch, mounted and wired

- Fan motor relay, mounted and wired

- 240/120 Volt, 60 Hz, 1.95/1.0 Amp, 130 CFM Max., 3200 RPM motor; Factory-wired for 240 Volt

- 90° elbow is used as a termination cap for horizontal venting

- Heavy-duty galvanized steel cabinet

- PolyTuf textured powder coat finish

- Indoor/Outdoor construction

- Easy installation

- Limited one-year warranty

- Shipped loose for field mounting

#### D-2 Power Vent

#### For Heater Models 206-407	Heater Model

| Heater Model | Power Vent Part No.* | Dimensions (in.) |  |
| --- | --- | --- | --- |
|  |  | B | D |
| 206/207 | 009832 | 12-3/8 | 4-1/4 |
| 266/267 | 009832 | 12-3/8 | 4-1/4 |
| 336/337 | 009833 | 18-1/8 | 7-1/4 |
| 406/407 | 009833 | 18-1/8 | 7-1/4 |

*	Part numbers are for 240 VAC units. 
Consult factory for 120 VAC units.

NOTES:

- All units can exhaust flue gases horizontally or vertically at up to 100 ft. of equivalent length vent pipe

-	90° elbow = 10 ft. equivalent length

-	45° elbow = 5 ft. equivalent length

2.	Vent pipe must meet Category III appliance venting requirements.

3.	Vent pipe sizes are based on 400°F nominal flue temperature and sea-level operation. For installation under other conditions, please consult the factory.