Job:

# Hi Delta® - Type P

## Commercial Pool Heaters Models 992B-1262B

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

Sealed Combustion Chamber

Standard “H” Bypass Shown

Patent No. 7,044,124

100% Factory Fire Tested

Efficiency: 85%

Minimum Non-condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-year Thermal Shock Warranty

Limited Five-year Heat Exchanger Warranty

Full Safety Diagnostics with Fault History

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-assisted

Proudly Assembled in the USA

Non-ferrous Bypass

Patented Burner Security Blanket

Heat Exchanger

- Brass Headers

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Cupro-Nickel Finned Tubing

- ASME Steel Tube Sheet

- Silicone High-Temp O-Rings

- 125 PSIG ASME Pressure Relief Valve

- Temperature and Pressure Gauge

- Water Connections

Left – Standard

Right – Option A-6

- Bronze Pump, 1/2 HP, 120V, 60Hz

- Non-ferrous Pool Bypass

Controls

- 120V, 60Hz, 1 Power Supply

- 120/24V 60Hz Transformer

- 100% Shut-off/Lockout

- Hot Surface Ignition System

- Remote Flame Sensor

- High Limit Control, Auto Reset

- On/Off Power Switch

- Manual Shut-off, Front-mounted

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switches

- Economaster Pump Time Delay

- Poolstat

- Diagnostics Panel with LCD Panel

- 2 Lines, 20 Characters

Gas Train

- Combination Valves

- On/Off Firing

- Low Gas Pressure Switch, Manual

- Fuel

Natural Gas

Propane Gas

- Design Certified ANSI Z21.56/
CSA 4.7

Burner

- Ultra-low NOx:
Less than 20 PPM

Construction

- Indoor/Outdoor Construction

- Enclosed Front Controls

- CSA Low Lead Certified ≤ .25% Lead

Venting

- Vent Location

Top – Standard

Rear – Option D-14

- Vent Termination Cap

Outdoor – Option D-11

Indoor, Horizontal – 
Option D-15

Indoor, Vertical (by others)

- Combustion Air

In-Line Filter Kit (TruSeal only) – Option D-17

Air Intake Elbow – 
Option D-16

Multi-Heater Controllers

B-26	2-Stage Digital

B-21	4-Stage Digital

B-__	TempTracker Mod+ (Up to 16 Boilers)

B-60	Stage Interface

Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

Left Side - Standard 
 Right Side - Optional

F-10		Low Water Cut-off, Remote Probe

P-__	Cold Water Run System

(See Page 3 Sizes 992B-1262B only)

S-2	High Gas Pressure Switch, Manual (Dual switches on Model 1532B)

X-1	SureRack® Kit (Lower Unit Requires Manifold Modification)

X-2	SureRack® Kit, Above Grade

Add-on (Used with X-1) (Lower Unit Requires Manifold Modification)

Regulatory Agency Requirements

For Metric information, see Catalog

G-1	CSD-1

Hi Delta – Type P

Models 992B-1262B (H-Bypass)		        				Model

Standard “H” Bypass

RATE OF FLOW AND PRESSURE DROP

| ###### Model | ###### Max. Flow |  |  |
| --- | --- | --- | --- |
|  | ###### GPM | ∆P (ft) | ###### ∆T |
| 992B | 132 | 14.0 | 13 |
| 1262B | 132 | 15.5 | 16 |

| Model | MBTUH |  | A | K | W | Amp Draw (w/ Pump) | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output | Width |  |  |  |  |
| 992B | 990 | 842 | 57-1/8 | 10 | 16-13/16 | < 16 | 900 |
| 1262B | 1260 | 1071 | 68-1/2 | 12 | 20-9/16 | < 16 | 1010 |

Dimensions are in inches.

Ratings shown are for elevations up to 4,500 feet and for natural or propane gas.

For installation at elevations over 4,500 feet, please contact manufacturer.

Hi Delta – Type P

Models 992B-1262B (Cold Water Run Bypass)				Model

| Model | MBTUH |  | A Width | K | W | Amp Draw (w/ Pump) | Pump HP | Injector Pump HP | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output |  |  |  |  |  |  |  |
| P 992B | 990 | 842 | 57-1/8 | 10 | 16-13/16 | < 16 | 1/2 | 1/3 * | 1000 |
| P 1262B | 1260 | 1071 | 68-1/2 | 12 | 20-9/16 | < 16 | 1/2 | 1/3 * | 1055 |

Dimensions are in inches.

Ratings shown are for elevations up to 4,500 feet and for natural or propane gas.

For installations at elevations over 4,500 feet, please contact manufacturer.

* Separate 120 VAC or 240 VAC 1Ø power required for Cold Water Run option.

Injector pump shipped loose for field installation at bypass inlet.

RATE OF FLOW AND PRESSURE DROP

| ###### Model | ###### Max. Flow |  |  |
| --- | --- | --- | --- |
|  | ###### GPM | ∆P (ft) | ###### ∆T |
| 992B | 132 | 14.0 | 13 |
| 1262B | 132 | 15.5 | 16 |

Raypak, Inc. ▪ 2151 Eastman Avenue, Oxnard, CA 93030 ▪ (805) 278-5300 ▪ Fax (805) 872-9725 ▪ www.raypak.com