Job:

# Hi Delta® - Type P

## Commercial Pool Heaters Models 302B & 402B

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

Sealed Combustion Chamber

Patent No. 7,044,124

100% Factory Fire Tested

Efficiency: 85%

Minimum Non-condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-year Thermal Shock Warranty

Limited Five-year Heat Exchanger Warranty

Diagnostic Center with Fault History

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-assisted

Proudly Assembled in the USA

Non-ferrous Bypass

Patented Burner Security Blanket

Standard “Sparcomatic” Bypass Shown

#### Heat Exchanger

- Brass Headers

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Cupro-Nickel Finned Tubing

- ASME Steel Tube Sheet

- Silicone High-Temp O-Rings

- 125 PSIG ASME Pressure Relief Valve

- Temperature and Pressure Gauge

- Water Connections

Left – Standard

Right – Option A-6

- Bronze Pump, 1/3 HP, 120V, 60Hz

- Non-Ferrous Pool Bypass Assembly with Automatic Control

#### Controls

- 120V, 60Hz, 1 Power Supply

- 120/24V 60Hz Transformer

- 100% Shut-off/Lockout

- Hot Surface Ignition

- Remote Flame Sensor

- High Limit Control, Auto Reset

- On/Off Power Switch

- Manual Shut-off, Front-mounted

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switch

- Pump Time Delay

- Poolstat

- Diagnostic Panel with LCD Display

- 2 Lines, 20 Characters

#### Gas Train

- Combination Valve

- On/Off Firing

- Fuel

Natural Gas

Propane Gas

- Design Certified ANSI Z21.56/
CSA 4.7

#### Burner

- Ultra-low NOx:
Less Than 20 PPM

#### Construction

- Indoor/Outdoor Construction

- Enclosed Front Controls

- CSA Low Lead Certified ≤ .25%

- Lead

#### Venting

- Vent Location

Top – Standard

Rear – Option D-14

- Vent Termination Cap

Outdoor – Option D-11

Indoor, Horizontal – 
Option D-15

Indoor, Vertical (by others)

- Combustion Air

In-Line Filter Kit (TruSeal 
only) – Option D-17

Air Intake Elbow – 
Option D-16

#### Multi-Heater Controllers

B-26	2-Stage Digital

B-21	4-Stage Digital

B-  	TempTracker Mod+ (Up to 16 Boilers)

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

F-10	Low Water Cut-Off, Remote Probe

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack® Kit (Lower Unit Requires Manifold Modification)

X-2	SureRack Add-on (Lower Unit Requires Manifold Modification)

#### Regulatory Agency Requirements

For Metric information, see Catalog

G-1	CSD-1

#### Hi Delta – Type P

#### Models 302B & 402B (“Sparcomatic” Bypass Option)	Model

RATES OF FLOW AND PRESSURE DROPS

| ###### Model | ###### Max. Flow |  |  |
| --- | --- | --- | --- |
|  | ###### GPM | ∆P (ft) | ###### ∆T |
| 302B | 90 | 9.8 | 6 |
| 402B | 90 | 10.0 | 8 |

| Model | MBTUH |  | A | K | W | Amp Draw (w/ Pump) | Operating Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output | Width |  |  |  |  |
| 302B | 300 | 255 | 36 | 5 | 14-3/4 | < 12 | 425 |
| 402B | 399 | 339 | 43 | 6 | 18-1/2 | < 12 | 500 |

NOTES:	Dimensions are in inches.

Ratings shown are for elevations up to 4,500 feet and for natural or propane gas.

For installation at elevations over 4,500 feet, please contact manufacturer.

#### Hi Delta – Type P

#### Models 302B & 402B (Cold Water Run Option)	Model

RATES OF FLOW AND PRESSURE DROPS

| ###### Model | ###### Max. Flow |  |  |
| --- | --- | --- | --- |
|  | ###### GPM | ∆P (ft) | ###### ∆T |
| 302B | 90 | 9.8 | 6 |
| 402B | 90 | 10.0 | 8 |

| Model | MBTUH |  | A | K | W | Amp Draw (w/ Pump) | Shipping Weight (Lbs.) | Pump HP | Injector Pump HP |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output | Width |  |  |  |  |  |  |
| 302B | 300 | 255 | 36 | 5 | 18 | < 12 | 425 | 1/2 | 1/4 |
| 402B | 399 | 339 | 43 | 6 | 18-1/2 | < 12 | 500 | 1/2 | 1/4 |

NOTES:	Dimensions are in inches.

Ratings shown are for elevations up to 4,500 feet and for natural or propane gas.

For installation at elevations over 4,500 feet, please contact manufacturer.

* Separate 120 VAC or 240 VAC 1Ø power required.

Injector pump ships loose for field installation at bypass inlet.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com