# MVB® - Type H

## Heating Boilers
Models 504A-2004A

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- 84% Thermal Efficiency at Full Rate

- 100% Factory Fire-Tested

- VERSA IC® Modulating Controller with 7” color touchscreen display

- Raymote™ remote connectivity provided standard

- Electronic Modulation, 60% Minimum Fire

- Full Safety Diagnostics with History

- Status Display Lights

- Modbus RTU BMS Port

- Maximum Outlet Water Temperature: 235°F

- Minimum Acceptable Inlet Water Temperature: 120°F

- Limited Twenty-Five-Year Thermal Shock Warranty

Proudly Assembled in the USA

Limited Ten-Year Heat Exchanger Warranty

- Ultra Low NOx – Less than 20PPM

#### Heat Exchanger

Headers

Cast Iron – Standard

A-1 Bronze

ASME H Stamped
160 PSIG MAWP

National Board Approved

Fin Tubing

Copper – Standard

A-3 Cupronickel

ASME Powder-Coated Tube Sheet

Silicone High-Temp O-Rings

ASME Pressure Relief Valve

60 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge,
Shipped Loose

Stainless Steel Evaporator Plate

Four-pass heat exchanger

#### Control

120V, 60Hz, 1Ø, Power Supply

120/24V 60Hz Transformer

VERSA IC® built-in control

7” color HD touchscreen display

Raymote™ Wi-Fi remote connectivity

Cascade up to 4 Boilers

Ignition Module

3-Try – Standard

C-6 Single-Try

Remote Flame Sensor

Freeze Protection

High Limit, Manual Reset, Fixed, 240ºF

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Programmable Pump Time Delays

Pump Outputs

Boiler pump

DHW Indirect – Pilot Duty

System – Pilot Duty

#### Control (cont.)

Water Temperature Sensors (7)

Modbus RTU BMS Port

- B-85	Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

- B-86	  Gateway - LonWorks

Cold Water Protection Function

- Optional Variable Speed Pump

- Optional Proportional Valve

#### Burner

Hot Surface Ignition (HSI)

Radially-Fired Knitted Burner

#### Gas Train

Fuel

Natural Gas

Propane (Minimum Grade HD-5)

Dual-Seat Combination Firing Valve

Manual Shut-Off Valve

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

PolyTuf Powder Coat Finish

Rear Connections (Water, Electrical, Gas, Vent, Combustion Air)

Combustion Air Filter – Inline

Design Certified ANSI Z21.13/CSA 4.9

CSA Low Lead Certified ≤.25% Lead

#### Venting

Vent Termination

D-11 Outdoor

D-15 Indoor, Horizontal

Indoor, Vertical (by others)

Combustion Air

D-16 Air Intake Elbow

Extractor – Optional

By others

Not required

- Options

A-30	Air Vent, Auto, 150 PSI (Loose)

B-31	Dry-Well Assembly

B-32	Outdoor Air Sensor

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit, Auto Reset, Adj., 
100-240F

I-2	High Limit, Manual Reset, Adj., 100-240F (additional)

P-  	Pump:      HP, 120V, 1, 60Hz

Cast Iron	 Bronze

Loose	 Mounted

P-  	Cold Water Start

P-  	Cold Water Run

S-1	Low Gas Pressure Switch, 
Manual Reset

S-2	High Gas Pressure Switch, Manual Reset

Z-12	Condensate Treatment Kit

#### Additional Options or Accessories

#### Multi-Boiler Temperature Controllers

TempTracker Mod+ Hybrid

B-36 2-4 Heaters

B-37 5-10 Heaters

B-38 11-16 Heaters

B-39 	EMS 4-20mA Remote Setpoint Interface Module

B-62  BACnet MS/TP Interface

MVB – Type H

Models 504A-2004A	Model

| Model (H7 - ) | Water Hardness |  |  |
| --- | --- | --- | --- |
|  | Soft | Medium | Hard |
| 504A | 1/4 – 6 | 1/4 – 6 | 3/4 – 11 |
| 754A | 1/4 – 6 | 1/2 – 7 | 3/4 – 11 |
| 1104A | 1/4 – 6 | 1/2 – 7 | 1 – 14 |
| 1504A | 3/4 – 11 | 1 – 14 | 1 – 14 |
| 2004A | 1 – 14 | 1-1/2 – 16 | 1-1/2 – 16 |

PUMP HP – AMPS*

* Current draw is for Pump Only

CLEARANCES

|  | Certified Minimum | Recomm. Service |
| --- | --- | --- |
| Front | 24” | 24” |
| Rear | 12” | 24” |
| Right | 1” | N/A |
| Left | 1” | N/A |
| Top | 0” | 10” |
| Floor | 0” | N/A |
| Vent | 1” | N/A |

| Model (H7-) | MBTUH |  |  | Dimensions (in.) |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | B Height | D | E | F | G* NPT | H NPT | K Flue Ø | L | M | N C/A Ø | P | R | V |
|  | Input | Output |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 504A | 500 | 420 | 43-1/4 | 30-3/4 | 35 | 23-3/4 | 1 | 2 | 8 | 13-3/4 | 14-1/4 | 6 | 36-3/4 | 8-1/4 | 1-3/4 |
| 754A | 750 | 630 | 49 | 36-3/4 | 40-3/4 | 29-1/2 | 1 | 2 | 10 | 13-1/2 | 14-1/4 | 6 | 42-1/2 | 8-1/4 | 1-3/4 |
| 1104A | 1100 | 924 | 55 | 42-3/4 | 46-3/4 | 35-1/2 | 1-1/4 | 2-1/2 | 10 | 13-1/2 | 14-1/4 | 6 | 48-1/2 | 8-1/4 | 1-3/4 |
| 1504A | 1500 | 1260 | 61 | 48-3/4 | 53 | 41-3/4 | 1-1/4 | 2-1/2 | 12 | 13-3/4 | 17-1/4 | 8 | 54-3/4 | 8-1/4 | 1-3/4 |
| 2004A | 1999 | 1679 | 75 | 61 | 65-1/4 | 53-3/4 | 2 | 2-1/2 | 14 | 13-1/2 | 20 | 8 | 68-1/2 | 9-1/4 | 5 |

- *For natural gas. Propane all sizes 1” NPT. - Ratings shown are for elevations up to 4,500 feet. For installations at elevations above 4,500 feet, please consult the factory for additional instructions. No hardware changes required below 10,000 ft. - For direct vent applications, please contact the factory about relocating the pump.

* Current draw is for Boiler Only.

(Supply breaker must have delayed trip.)

| Model (H7 - ) | Shipping Weight (Lbs.) | Footprint (ft2) | Amps* |
| --- | --- | --- | --- |
| 504A | 600 | 5.4 | 12 |
| Raypak, Inc. 2151 Eastman Avenue, Oxnard, CA 93030 (805) 278-5300 Fax (800) 872-9725 www.raypak.com 754A | 670 | 5.4 | 12 |
| 1104A | 720 | 5.4 | 12 |
| 1504A | 780 | 5.4 | 12 |
| 2004A | 940 | 5.4 | 18 |

MVB – Type H

Models 504A-2004A	Model

RATES OF FLOW AND PRESSURE DROPS

| Model (H7-) | 20°F T |  | 30°F T |  | 39°F T* |  | Maximum Flow |  |  | Minimum Flow* |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | GPM | P (ft.) | GPM | P (ft.) | GPM | P (ft.) | GPM | P (ft.) | T (°F) | GPM | P (ft.) | T (°F) |
| 504A | 42 | 2.7 | 28 | 1.4 | N/A | N/A | 100 | 11.3 | 8 | 25 | 1.1 | 34 |
| 754A | 63 | 6.0 | 42 | 2.9 | 32 | 1.7 | 100 | 13.8 | 13 | 32 | 1.7 | 39 |
| 1104A | 92 | 13.3 | 62 | 6.7 | 47 | 4.1 | 113 | 18.6 | 16 | 47 | 4.1 | 39 |
| 1504A | N/A | N/A | 84 | 13.3 | 65 | 8.0 | 113 | 22.2 | 22 | 65 | 8.0 | 39 |
| 2004A | N/A | N/A | 112 | 26.9 | 86 | 16.0 | 113 | 27.2 | 30 | 86 | 16.0 | 39 |

* Closed systems only

Raypak, Inc. • 2151 Eastman Avenue, Oxnard, CA 93030 • (805) 278-5300 • (Fax (800) 872-9725 • www.raypak.com