Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

100% Factory Fire Tested

Efficiency: 85%

Maximum Outlet Temperature: 210°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Year Thermal Shock Warranty

Limited Five-Year Heat Exchanger Warranty

Full Safety Diagnostics with Fault History

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-Assisted

Patented Burner Security Blanket

#### Heat Exchanger

HLW Stamp

Headers

Brass – Standard

Glass-Lined Cast Iron – 
Option A-2

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone High Temp. O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

Right – Option A-6

#### Controls

120V, 60Hz, 1( Power Supply

120/24V 60Hz Transformer

100% Shut-Off/Lockout

Hot Surface Ignition

Remote Flame Sensor

High Limit Control, Manual Reset

On/Off Power Switch

Manual Shut-Off, Front-Mounted

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switches

Economaster Pump Time Delay

Enable/Disable

Diagnostics Panel with LCD Display

2 Lines, 20 Characters

#### Gas Train

Manual Gas Shut-Off Valve(s)

Combo Valve(s)

Firing Mode

3-Stage: Model 992B

4-Stage: Models 1262B-2342B

Fuel

Natural Gas

Propane Gas

4” WC Gas Supply Pressure
G-20

Design Certified - ANSI Z21.10.3/
CSA 4.3

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

CSA Low Lead Certified ≤ .25% Lead

#### Venting

Vent Location

Top – Standard

Rear – Option D-14

Vent Termination Cap

Outdoor  D-11

Indoor, Horizontal  D-15

Indoor, Vertical (by others)

Combustion Air

In-Line Filter Kit (TruSeal 
only)  D-17

Air Intake Elbow  D-16

Extractor – Optional

By others

Not required

#### Burner

Ultra-Low NOx: Less than 20 PPM

#### Temperature Controls

B-2	Tankstat, Single-Stage (100-200°F)

B-3	Tankstat, 2-Stage (100-200°F)

B-21	TempTracker Digital Controller, 
4-Stage

B-  	TempTracker Mod+ (loose) up to 16

B-60	Stage Interface

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1(, 60Hz Water Hardness:       GPG

Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Run (See 1000.19)

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

#### Regulatory Agency Requirements

#### Hi Delta – Type WH
Models 992B-2342B	Model

# Text boxes

# Hi Delta® - Type WH

## Water Heaters
Models 992B-2342B

Patent No. 7,044,124

Proudly Assembled in the USA

For Metric information, see Catalog

For Metric information, see Catalog

For Metric information, see Catalog

For Metric information, see Catalog

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com

NOTE:  Pump location varies based on model and application.

RECOVERY RATES (GPH)

|  | Temperature Rise in °F |
| --- | --- |
| Model | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 100° |
| 992B | 5100 | 3400 | 2550 | 2040 | 1700 | 1457 | 1275 | 1133 | 1020 |
| 1262B | 6491 | 4327 | 3245 | 2596 | 2164 | 1855 | 1623 | 1442 | 1298 |
| 1532B | 7882 | 5255 | 3941 | 3153 | 2627 | 2252 | 1970 | 1752 | 1576 |
| 1802B | 9273 | 6182 | 4636 | 3709 | 3091 | 2649 | 2318 | 2061 | 1855 |
| 2002B | 10298 | 6865 | 5149 | 4119 | 3433 | 2942 | 2574 | 2288 | 2060 |
| 2072B | 10664 | 7109 | 5332 | 4265 | 3555 | 3047 | 2666 | 2370 | 2133 |
| 2342B | 12055 | 8036 | 6027 | 4822 | 4018 | 3444 | 3014 | 2679 | 2411 |

SPECIFICATIONS

|  |  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH | Firing | A | H | K | T | W | Amp. | Shipping |
| Model | Input | Output | Stages | Width | NPT |  |  |  | Draw* | Wt. (Lbs.) |
| 992B | 990 | 842 | 3 | 57-1/8 | 2-1/2 | 10 | 10 | 16-13/16 | <12 | 900 |
| 1262B | 1260 | 1071 | 4 | 68-1/2 | 2-1/2 | 12 | 10 | 20-9/16 | <12 | 1010 |
| 1532B | 1530 | 1301 | 4 | 79-7/8 | 2-1/2 | 12 | 10 | 24-3/8 | <12 | 1225 |
| 1802B | 1800 | 1530 | 4 | 91-1/8 | 2-1/2 | 14 | 10 | 28-1/8 | <12 | 1350 |
| 2002B | 1999 | 1699 | 4 | 102-1/2 | 2-1/2 | 14 | 10 | 31-15/16 | <12 | 1450 |
| 2072B | 2070 | 1760 | 4 | 102-1/2 | 2-1/2 | 14 | 10 | 31-15/16 | <12 | 1450 |
| 2342B | 2340 | 1989 | 4 | 113-7/8 | 2-1/2 | 16 | 10 | 35-11/16 | <12 | 1520 |

Dimensions are in inches.	* Without pump

NOTES:	1. Rates shown are for natural or propane gas, and elevations up to 5,000 feet. For installation above 5,000 feet, please contact manufacturer.

2. Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.