Job:

# Raytherm® - Type H

## Hydronic Heating Boilers
Commercial

Models 514-824

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:

EFFICIENT

- 82% thermal efficiency – highest of any atmospheric
boiler available today

THERMAL SHOCK PROOF

- Twenty-year warranty against thermal shock damage
up to 150°F differential

- Maximum operating temperature: 230°F

LIGHTWEIGHT

- A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

- Cuts fuel costs substantially because the standby and radiation losses normal to other boilers are eliminated

LOW WATER OPERATING TEMPERATURE

Proudly Assembled in the USA

Operates with inlet water temperature as low as 105°F
without condensing

#### Heat Exchanger

- ASME Inspected and Stamped
160 PSIG

- National Board Listed

- Headers

Glass-lined Cast Iron – Standard

Bronze – Option A-1

- Finned Tubing

Copper – Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone O-Rings

- 60 PSIG ASME Pressure Relief Valve

- Temperature and Pressure Gauge

- Water Connections

Left Hand – Standard

Right Hand – Option A-6

- Pump, Rear-mounted – Optional

4.25” Impeller

4.7” Impeller

#### Controls

- 120V, 60Hz, 1 Ph Power Supply

- 120/24V Transformer

- 100% Pilot Shut-off/Lockout

- Electronic, Intermittent Ignition (IID) Pilot

- High Limit Control, Manual Reset

- On/Off Switch

- Flow Switch

- Economaster Pump Time Delay

#### Gas Train

- Manual Main Gas Shut-off Cock

- Main Gas Pressure Regulator

- Redundant Safety Shut-off Valve

- Control Valve

- Firing Mode

On/off (H4)

Two-stage Firing (H3)

Four-stage Firing (H9)

Mechanical Modulation,
110-170°F (H5)

Mechanical Modulation, 
150-210°F (H1)

Motorized Modulation (H2)

- Fuel

Natural Gas

Propane Gas

- Design Certified ANSI Z21.13/CSA 4.9

#### Construction

- CSA Low Lead Certified ≤ .25% Lead

- Front Controls

- Stainless Steel Burners

- Polytuf Powder Coat Finish

- Vent Selection

Draft Diverter (Indoor) – Option D-10

Power Vent, Loose (Indoor) – 
Option D-2

Stackless Top (Outdoor) – 
Option D-11

- Base (Optional)

Combustible Floor Shield

#### Temperature Controllers

- Note:  H1 and H5 require a system controller

B-6	Two-stage-Mechanical

B-40	Motorized Modulation

B-41	Motorized Modulation, outdoor reset

B-   	Two-stage Digital

B-   	Four-stage Digital

B-35	4-20 mA

B-60	Stage Interface

B-   	TempTracker Mod+ Hybrid 2-16 Boilers

#### Additional Safety Controls

F-9	Low Water Cut-off Probe

I-1	High Limit Control, Auto Reset

S-1	Low Gas Pressure Switch

S-2	High Gas Pressure Switch

#### Regulatory Agency Requirements

Raytherm - Type H

Hydronic Heating Boilers	Model

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

| Model No. | 10º ΔT |  | 20º ΔT |  | 30º ΔT |  | Minimum Flow |  |  | Maximum Flow |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | GPM | ΔP FT | GPM | ΔP FT | GPM | ΔP FT | GPM | ΔP (ft) | ΔT | GPM | ΔP (ft) | ΔT |
| H-514 | 84 | 7.8 | 42 | 1.9 | N/A | N/A | 40 | 1.8 | 21 | 90 | 9 | 9 |
| H-624 | N/A | N/A | 52 | 3.0 | N\A | N\A | 40 | 1.9 | 26 | 90 | 9.5 | 12 |
| H-724 | N/A | N/A | 60 | 4.4 | 40 | 2.0 | 40 | 2.0 | 30 | 90 | 10 | 13 |
| H-824 | N/A | N/A | 68 | 6.0 | 46 | 2.8 | 40 | 2.1 | 34 | 90 | 10.5 | 15 |

N/A – Not Applicable

BOILER RATE OF FLOW AND PRESSURE DROP

MODELS H 514-824

|  | Indoor and Outdoor |  | Dimensions (Inches) |  |  | Electrical Rating |  | Approx. Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model Number | MBTU Input (a) | MBTU Output (a) | Width A | Flue Dia. K | L | With Pump | Without Pump |  |
| H-514 | 511.5 | 419.4 | 32-3/4 | 10 | 25-3/8 | Less than 10 amps @ 120 V | Less than 4 amps @ 120V | 455 |
| H-624 | 627.0 | 514.0 | 37-1/2 | 12 | 29-1/2 |  |  | 465 |
| H-724 | 726.0 | 595.0 | 41-5/8 | 12 | 34-1/4 |  |  | 575 |
| H-824 | 825.0 | 676.5 | 45-3/4 | 14 | 38-1/2 |  |  | 605 |

Note: 	Ratings shown are for elevations up to 2,000 feet. For elevations over 2,000 feet, reduce ratings

at the rate of 4% for each 1,000 feet above sea level.

(a) Propane Input/Output is 94% of stated value.

.

.