Job:

# Raytherm® - Type WH

## Water Heaters
Commercial

Model 133

Engineer:

Contractor:

Prepared By: 	     		 Date:

Indoor/Outdoor:

EFFICIENT

INDOOR MODEL ILLUSTRATED

- 82% thermal efficiency – highest of any atmospheric water heater available today

THERMAL SHOCK PROOF

- Twenty-year warranty against thermal shock damage
up to 150°F differential

- Maximum operating temperature: 210°F

LIGHTWEIGHT

- A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

- Cuts fuel costs substantially because the standby and 
radiation losses associated with tank-type water heaters
are eliminated

LOW WATER OPERATING TEMPERATURE

- Operates with water temperature as low as
105°F without condensing

#### Heat Exchanger

- ASME Inspected and Stamped
160 PSIG

- National Board Approved

- Bronze Headers

- Copper Fin Tubing

- ASME Steel Tube Sheet

- Silicone O-Rings

- 125 PSIG ASME Pressure Relief Valve

- Temperature and Pressure Gauge,
Shipped Loose

- Four-pass Heat Exchanger

- Pump – Optional

Mounted, 1/8 HP, 120 VAC, 1 60 Hz

#### Controls

- 120V, 60Hz, 1 Ph Power Supply

- 120/24V Transformer

- 100% Pilot Shut-off/Lockout

- Electronic, Intermittent Ignition (IID) Pilot

- High Limit Control, Auto Reset – 200°F

- On/Off Switch

- Flue Gas Spillage Switch

- Economaster II Pump Time Delay

- Flame Roll-out Sensor

#### Gas Control Train

- Manual Main Gas Shut-off Cock

- Main Gas Pressure Regulator

- Redundant Safety Shut-off Valve

- Control Valve

- Firing Mode

On/Off (WH1)

Mechanical Modulation (WH2)

- Fuel

Natural Gas

Propane Gas

- Design Certified ANSI Z21.10.3

#### Construction

- Front Controls

- Stainless Steel Burners

- PolyTuf Powder Coat Finish

- Vent Selection

Drafthood (Indoor) – 
Option D-10

Stackless Top (Outdoor) – 
Option D-11

High-Wind Top (Outdoor) – 
Option D-13

- Base – Optional

Combustible Floor Shield – 
Option J-1

- CSA Low Lead Certified ≤ .25 Pb

- Temperature Controls

B-2	Single-Stage Tankstat 
(100-180°F)

B-3	2-Stage Tankstat (100-180°F)

B-26	2-Stage Digital (Loose)

B-21	4-Stage Digital (Loose)

#### Additional Safety Controls

Raytherm – Type WH

Model 133

| Model No. | INDOOR |  | OUTDOOR | Approx. Shipping Weight (Lbs.) |  |
| --- | --- | --- | --- | --- | --- |
|  | Input MBTUH | Output MBTUH | Output MBTUH | Without Pump | With Pump |
| WH-133 | 136 | 112 | 109 | 160 | 186 |

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

NOTES:	Dimensions are in inches.

Ratings shown are for elevations up to 2,000 feet. For elevations over 2,000 feet, reduce ratings 4% for 
each 1,000 feet above sea level.

###### HEATER RATES OF FLOW AND PRESSURE DROPS

| 10T |  | 20T |  | 30T |  | 40T |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GPM | P (ft) | GPM | P (ft) | GPM | P (ft) | GPM | P (ft) |
| 22 | 14.7 | 11 | 3.8 | N/A | N/A | N/A | N/A |

HEATER RECOVERY RATES (GPH)

|  | Temperature Rise |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20°F | 30°F | 40°F | 50°F | 60°F | 80°F | 100°F |
| INDOOR | 669 | 446 | 335 | 268 | 223 | 167 | 134 |
| OUTDOOR | 653 | 435 | 327 | 261 | 218 | 163 | 131 |