Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

100% Factory Fire Tested

Efficiency: 84%

Maximum Outlet Temperature: 230°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Year Thermal Shock Warranty

Limited Ten-Year Closed-System Heat Exchanger Warranty

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-Assisted

Patented Burner Security Blanket

#### Heat Exchanger

H Stamp

Headers

Glass-Lined Cast Iron – Standard

Bronze – Option A-1

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone High Temp O-Rings

Pressure Relief Valve, ASME

45 PSIG – Standard on Model 399B

60 PSIG – Standard on Models 499B-899B

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

Right – Option A-6

#### Controls

120V, 60Hz, 1 Phase Power Supply

120/24V 60Hz Transformer

100% Shut-Off/Lockout

Hot Surface Ignition

Remote Flame Sensor

High Limit Control, Manual Reset

On/Off Power Switch

Manual Shut-Off, Front-Mounted Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Pump Time Delay Relay

Status Display Lights

#### Gas Train

Manual Gas Shut-Off Valve(s)

Combination Valves

Firing Mode

On/Off: Model 399B

2-Stage: Models 
499B-899B

Fuel

Natural Gas

Propane Gas

Design Certified - ANSI Z21.13/CSA 4.9

#### Burner

Ultra-Low NOx: Less than 
20 PPM

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

CSA Low Lead Certified (≤ .25% Lead)

#### Venting

Vent Location

Top, Outdoor – Standard

Top, Indoor – Option D-20

Rear – Option D-14

Vent Termination Cap

Outdoor D-11

Indoor, Horizontal D-15

Indoor, Vertical (by others)

Extractor – Optional

By others

Not required

#### Temperature Controls

B-6	Aquastat, 2-Stage (100-200°F)

B-  	TempTracker Digital Controller,   2-Stage (Loose)

B-  	TempTracker Digital Controller,   4-Stage (Loose)

B-  	TempTracker Mod+ Hybrid (2-16 Boilers)

B-60	Stage Interface

#### Options

C-6	Ignition Module, Manual Reset

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1(, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Start (See 2000.48)

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

#### Regulatory Agency Requirements

#### Delta Limited – Type H

#### Models 399B-899B	Model

# Text boxes

# Delta Limited™ - Type H

## Space Heating/Hot Water Boilers Models 399B-899B

Shown with outdoor 
air inlet and pump covers

Proudly Assembled in the USA

Delta Limited models not approved for use in California

For Metric information, see Catalog

For Metric information, see Catalog

Raypak, Inc. ( 2151 Eastman Avenue, Oxnard, CA  93030 ( (805) 278-5300 ( Fax (800) 872-9725 ( www.raypak.com

NOTE: Pump location varies based on model selected

SPECIFICATIONS

|  |  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH | A | G | H | K | T | W | Amp. | Shipping |
| Model | Input | Output | Width | NPT | NPT |  |  |  | Draw* | Wt. (Lbs) |
| 399B | 399 | 335 | 43 | ¾ | 2 | 6 | 6 | 18-1/2 | < 6 | 445 |
| 499B | 500 | 420 | 50 | 1 ¼ | 2 | 6 | 6 | 22 | < 6 | 545 |
| 649B | 650 | 546 | 60 ½ | 1 ¼ | 2 | 8 | 6 | 27-1/4 | < 6 | 590 |
| 749B | 750 | 630 | 67 ½ | 1 ¼ | 2 | 8 | 6 | 30-3/4 | < 6 | 675 |
| 899B | 900 | 756 | 78 | 1 ¼ | 2 | 8 | 6 | 36 | < 7 | 740 |

* Pump not included

Dimensions are in inches.

Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

Recommended natural gas supply pressure is 7 – 10.5” WC. Recommended propane gas supply pressure is 11 - 13” WC.

RATES OF FLOW AND PRESSURE DROPS

|  | 10°F ∆T | 20°F ∆T | 30°F ∆T | Min. Flow | Max. Flow |
| --- | --- | --- | --- | --- | --- |
| Model | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) | ∆T | GPM | ∆P (ft) | ∆T |
| 399B | 68 | 5.4 | 34 | 1.5 | 22 | <1 | 20 | <1 | 34 | 90 | 10.0 | 7 |
| 499B | 85 | 9.2 | 42 | 2.3 | 28 | 1.1 | 21 | <1 | 40 | 90 | 10.5 | 9 |
| 649B | N/A | N/A | 55 | 4.0 | 36 | 1.8 | 28 | 1.1 | 40 | 90 | 10.7 | 12 |
| 749B | N/A | N/A | 64 | 5.5 | 42 | 2.5 | 32 | 1.6 | 40 | 90 | 11.0 | 14 |
| 899B | N/A | N/A | 76 | 8.5 | 51 | 3.8 | 38 | 2.2 | 40 | 90 | 11.8 | 16 |

Basis is 20 GPM or 40°F ∆T for minimum flow, 90 GPM for maximum flow.