Job:

# Delta Limited™ - Type H

## Space Heating/Hot Water Boilers Models 399B-899B

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

Shown with outdoor 
air inlet and pump covers

100% Factory Fire Tested

Efficiency: 84%

Maximum Outlet Temperature: 230°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Year Thermal Shock Warranty

Limited Ten-Year Closed-System Heat Exchanger Warranty

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-Assisted

Proudly Assembled in the USA

Patented Burner Security Blanket

#### Heat Exchanger

- H Stamp

- Headers

Glass-Lined Cast Iron – Standard

Bronze – Option A-1

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone High Temp O-Rings

- Pressure Relief Valve, ASME

45 PSIG – Standard on Model 399B

60 PSIG – Standard on Models 499B-899B

PSIG – Optional

- Temperature and Pressure Gauge

- Water Connections

Left – Standard

Right – Option A-6

#### Controls

- 120V, 60Hz, 1 Phase Power Supply

- 120/24V 60Hz Transformer

- 100% Shut-Off/Lockout

- Hot Surface Ignition

- Remote Flame Sensor

- High Limit Control, Manual Reset

- On/Off Power Switch

- Manual Shut-Off, Front-Mounted Switch

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switch

- Pump Time Delay Relay

- Status Display Lights

#### Gas Train

- Manual Gas Shut-Off Valve(s)

- Combination Valves

- Firing Mode

On/Off: Model 399B

2-Stage: Models 
499B-899B

- Fuel

Natural Gas

Propane Gas

- Design Certified - ANSI Z21.13/CSA 4.9

#### Burner

- Ultra-Low NOx: Less than 
20 PPM

#### Construction

- Indoor/Outdoor Construction

- Enclosed Front Controls

- CSA Low Lead Certified (≤ .25% Lead)

#### Venting

- Vent Location

Top, Outdoor – Standard

Top, Indoor – Option D-20

Rear – Option D-14

- Vent Termination Cap

Outdoor D-11

Indoor, Horizontal D-15

Indoor, Vertical (by others)

- Extractor – Optional

By others

Not required

Temperature Controls

Delta Limited models not approved for use in California

B-6	Aquastat, 2-Stage (100-200°F)

B-  	TempTracker Digital Controller,   2-Stage (Loose)

B-  	TempTracker Digital Controller,   4-Stage (Loose)

B-  	TempTracker Mod+ Hybrid (2-16 Boilers)

B-60	Stage Interface

#### Options

C-6	Ignition Module, Manual Reset

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Start (See 2000.48)

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

For Metric information, see Catalog

#### Regulatory Agency Requirements

For Metric information, see Catalog

#### Delta Limited – Type H

#### Models 399B-899B	Model

Raypak, Inc.  2151 Eastman Avenue, Oxnard, CA  93030  (805) 278-5300  Fax (800) 872-9725  www.raypak.com

NOTE: Pump location varies based on model selected

SPECIFICATIONS

|  |  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH |  | A | G | H | K | T | ###### W | ###### Amp. | Shipping |
| ###### Model | ###### Input | Output | Width | ###### NPT | NPT |  |  |  | ###### Draw* | Wt. (Lbs) |
| 399B | 399 | 335 | 43 | ¾ | 2 | 6 | 6 | 18-1/2 | < 6 | 445 |
| 499B | 500 | 420 | 50 | 1 ¼ | 2 | 6 | 6 | 22 | < 6 | 545 |
| 649B | 650 | 546 | 60 ½ | 1 ¼ | 2 | 8 | 6 | 27-1/4 | < 6 | 590 |
| 749B | 750 | 630 | 67 ½ | 1 ¼ | 2 | 8 | 6 | 30-3/4 | < 6 | 675 |
| 899B | 900 | 756 | 78 | 1 ¼ | 2 | 8 | 6 | 36 | < 7 | 740 |

* Pump not included

Dimensions are in inches.

Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

Recommended natural gas supply pressure is 7 – 10.5” WC. Recommended propane gas supply pressure is 11 - 13” WC.

RATES OF FLOW AND PRESSURE DROPS

|  | 10°F ∆T |  | 20°F ∆T |  | 30°F ∆T |  | ###### Min. Flow |  |  | ###### Max. Flow |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### Model | ###### GPM | ∆P (ft) | ###### GPM | ∆P (ft) | ###### GPM | ∆P (ft) | ###### GPM | ∆P (ft) | ###### ∆T | ###### GPM | ∆P (ft) | ###### ∆T |
| 399B | 68 | 5.4 | 34 | 1.5 | 22 | <1 | 20 | <1 | 34 | 90 | 10.0 | 7 |
| 499B | 85 | 9.2 | 42 | 2.3 | 28 | 1.1 | 21 | <1 | 40 | 90 | 10.5 | 9 |
| 649B | N/A | N/A | 55 | 4.0 | 36 | 1.8 | 28 | 1.1 | 40 | 90 | 10.7 | 12 |
| 749B | N/A | N/A | 64 | 5.5 | 42 | 2.5 | 32 | 1.6 | 40 | 90 | 11.0 | 14 |
| 899B | N/A | N/A | 76 | 8.5 | 51 | 3.8 | 38 | 2.2 | 40 | 90 | 11.8 | 16 |

Basis is 20 GPM or 40°F ∆T for minimum flow, 90 GPM for maximum flow.