Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

- 100% Factory Fire Tested

- Efficiency: 84%

- Maximum Outlet Temperature: 230°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal Shock Proof Heat Exchanger

- Limited Twenty-Year Thermal Shock Warranty

- Limited Ten-Year Closed-System Heat Exchanger Warranty

- Full Safety Diagnostics with Fault History

- PolyTuf Powder Coated Cabinet

Patent No. 7,044,124

- No Combustible Floor Shield Required

- Fan-Assisted

- Patented Burner Security Blanket

#### Heat Exchanger

H Stamp

Headers

Glass-Lined Cast Iron – Standard

Brass – Option A-1

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone High Temp. O-Rings

ASME Pressure Relief Valve

45 PSIG – Standard on Models  302B and 402B

60 PSIG – Standard on Models 502B-902B

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

Right – Option A-6

#### Controls

120V, 60Hz, 1( Power Supply

120/24V 60Hz Transformer

100% Shut-Off/Lockout

Hot Surface Ignition

Remote Flame Sensor

High Limit Control, Manual Reset

On/Off Power Switch

Manual Shut-Off, Front-Mounted

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Economaster Pump Time Delay

Enable/Disable

Diagnostics Panel with LCD Display 2 Lines, 20 Characters

#### Gas Train

Manual Gas Shut-Off Valve(s)

Combo Valve(s)

Firing Mode

On/Off (H4): Models 
302B and 402B

2-Stage (H3): Models 
302B-902B

Fuel

Natural Gas

Propane Gas

4” WC Gas Supply Pressure
(G-20)

Design Certified ANSI Z21.13/
CSA 4.9

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

CSA Low Lead Certified (≤ .25% Lead)

#### Venting

Vent Location

Top – Standard

Rear – Option D-14

Vent Termination Cap

Outdoor  D-11

Indoor, Horizontal  D-15

Indoor, Vertical (by others)

Combustion Air

In-Line Filter Kit (TruSeal only)
D-17

Air Intake Elbow  D-16

Extractor – Optional

By others

Not required

#### Burner

Ultra-Low NOx: Less than 20 PPM

#### Temperature Controls

B-6	Aquastat, 2-Stage (100-200°F)

B-  	TempTracker Digital Controller,
2-Stage

B-  	TempTracker Digital Controller,
4-Stage

B-  	TempTracker Mod+ Hybrid (2-16 Boilers)

B-60	Stage Interface

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal( Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1(, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Start (See 2000.48)

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

#### Regulatory Agency Requirements

#### Hi Delta – Type H

#### Models 302B-902B 	Model

# Text boxes

# Hi Delta( - Type H

## Space Heating/Hot Water Boilers Models 302B-902B

Proudly Assembled in the USA

For Metric information, see Catalog

For Metric information, see Catalog

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

2.	Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.

SPECIFICATIONS

|  |  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH | A | G | H | K | T | W | Amp. | Shipping |
| Model | Input | Output | Width | NPT | NPT |  |  |  | Draw | Wt. (Lbs) |
| 302B | 300 | 252 | 36 | 3/4 | 2 | 5 | 6 | 18 | 6 | 380 |
| 402B | 399 | 335 | 43 | 3/4 | 2 | 6 | 6 | 18-1/2 | 6 | 445 |
| 502B | 500 | 420 | 50 | 1-1/4 | 2 | 6 | 6 | 22 | 6 | 545 |
| 652B | 650 | 546 | 60-1/2 | 1-1/4 | 2 | 8 | 6 | 27-1/4 | 6 | 590 |
| 752B | 750 | 630 | 67-1/2 | 1-1/4 | 2 | 8 | 6 | 30-3/4 | 6 | 675 |
| 902B | 900 | 756 | 78 | 1-1/4 | 2 | 8 | 6 | 36 | 7 | 740 |

Dimensions are in inches.

NOTE: Pump location varies based on model and application

RATES OF FLOW AND PRESSURE DROPS

|  | 10°F ∆T | 20°F ∆T | 30°F ∆T | Min. Flow | Max. Flow |
| --- | --- | --- | --- | --- | --- |
| Model | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) | ∆T | GPM | ∆P (ft) | ∆T |
| 302B | 51 | 3.2 | 25 | <1.0 | N/A | N/A | 20 | <1 | 25 | 90 | 9.8 | 6 |
| 402B | 68 | 5.4 | 34 | 1.5 | 22 | <1 | 20 | <1 | 34 | 90 | 10.0 | 7 |
| 502B | 85 | 9.2 | 42 | 2.3 | 28 | 1.1 | 21 | <1 | 40 | 90 | 10.5 | 9 |
| 652B | N/A | N/A | 55 | 4.0 | 36 | 1.8 | 28 | 1.1 | 40 | 90 | 10.7 | 12 |
| 752B | N/A | N/A | 64 | 5.5 | 42 | 2.5 | 32 | 1.6 | 40 | 90 | 11.0 | 14 |
| 902B | N/A | N/A | 76 | 8.5 | 51 | 3.8 | 38 | 2.2 | 40 | 90 | 11.8 | 17 |

Basis is 20 GPM or 40°F ∆T for minimum flow, 90 GPM for maximum flow.