Job:

# SureRack® Kit

## Stacking System for
Hi Delta® Boilers

## Models 302B-2342B

Engineer:

Contractor:

Prepared By:

Model:  	     		Date:

Features

- Two-boiler Vertical Stack

- No Vent Offset Required

- Small Footprint

- Low Ceiling Height

- Heavy Duty Construction

See installation manual 240792

| Hi Delta Model | SureRack Kit (X-1) |  |  |  |  |  | Above-Grade Add-On (X-2) | Stacked Boiler Height (in.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Part No. | Weight (lbs.) | Dimensions (in.) |  |  | Cross Beams |  |  |
|  |  |  | A | B | W |  |  |  |
| 302B | 006906 | 201 | 30 | 41-1/4 | CTR. | 3 | P/N 007046 | 72-1/4 |
| 402B | 006907 | 214 |  | 48-1/4 |  |  |  |  |
| 502B | 006908 | 228 |  | 55-1/4 |  |  |  |  |
| 652B | 006909 | 257 |  | 65-3/4 |  |  |  |  |
| 752B | 006910 | 265 |  | 72-3/4 |  |  |  |  |
| 902B | 006911 | 276 |  | 83-1/4 |  |  |  |  |
| 992B | 011563 | 340 | 37-1/2 | 64-1/8 | 16-13/16 | 4 | P/N 007053 | 87-1/2 |
| 1262B | 011564 | 361 |  | 75-1/2 | 20-9/16 |  |  |  |
| 1532B | 011565 | 371 |  | 87 | 26-3/8 |  |  |  |
| 1802B | 011566 | 408 |  | 98-1/8 | 30-1/8 |  |  |  |
| 2002B | 011567 | 430 |  | 109-1/2 | 33-15/16 |  |  |  |
| 2072B | 011567 | 430 |  | 109-1/2 | 33-15/16 |  |  |  |
| 2342B | 011568 | 458 |  | 121 | 37-11/16 |  |  |  |

#### SureRack Kit
For Hi Delta 302B-2342B	Model

Anchoring Information

| For reference only. Recommended to match drill on job site. Hi Delta Model | Anchoring Dimensions (in.) |  |  |
| --- | --- | --- | --- |
|  | A | B | C |
| 302B | 34-1/4 | 24 | 2-1/4 |
| 402B | 42-1/4 |  |  |
| 502B | 49-1/4 |  |  |
| 652B | 59-3/4 |  |  |
| 752B | 66-3/4 |  |  |
| 902B | 77-1/4 |  |  |
| 992B | 56-1/8 | 31-9/16 | 3-1/4 |
| 1262B | 67-7/16 |  |  |
| 1532B | 78-3/4 |  |  |
| 1802B | 90-1/8 |  |  |
| 2002B | 101-1/2 |  |  |
| 2072B |  |  |  |
| 2342B | 112-13/16 |  |  |

- Use a minimum of two bolts ½” x 5”, 
A-307 Grade 5.2 or equivalent. Use Hilti HY-150 adhesive to secure expansion anchor. For additional information see SureRack Kit installation instructions.

- Approved for all installations.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

HOUSEKEEPING PAD