Job:

# ADB™ - Type WH

## Water Heaters

Models 751-1501

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

100% Factory Fire Tested

- Efficiency: 84%

- Maximum Outlet Temperature: 210°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal Shock Proof Heat Exchanger

- Footprint: Less Than 5-1/2 ft2

- Limited Twenty-Year Thermal Shock Warranty

- Limited Ten-Year Heat Exchanger Warranty

- Ten-Year Unconditional Burner Head Warranty

- Operation Status Center and Full Diagnostic Panel

#### Heat Exchanger

- Bronze Headers

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Finned Cupro-Nickel Tubes

- ASME Steel Tube Retainer

- Silicone High Temp O-Rings

- 125 PSIG ASME Pressure Relief Valve

- Temperature and Pressure Gauge, Shipped Loose

#### Control

- 120V, 60Hz, Power Supply

- 120/24V 60Hz Transformer

- 100% Pilot Shutoff/Lockout

- Pilot: Electronic Intermittent Ignition (I.I.D.)

- High Limit Control, Manual Reset

- High Limit Control, Auto Reset

- On/Off Switch

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switch

- Time Delay Pump Off Control

- Central Point Wiring Diagnostics Panel

#### Burner

- Aerodynamically Stabilized
Non-Clog  Burner

- Ultra-Low NOx: Less than 30 PPM

#### Gas Train

- Fuel

Natural Gas

Propane (Models 751 & 1001)

- Manual Gas Shut-off Valves

- Gas Pressure Regulator

- Safety Shut-off Valve

- Firing Control Valve

- Low Gas Pressure Switch, Manual

- On/Off Firing Mode

- Design Certified ANSI Z21.10.3

#### Construction

- Indoor/Outdoor Construction

- Front Controls Enclosed

- PolyTuf Powder Coat Finish

- Connections (Water, Electrical, Gas)

Rear – Standard

Right Side – Option A-8

#### Venting

- Vent Location

Rear – Standard

Right Side – Option Z-2

- Vent Termination Cap

Outdoor – Option D-11

Indoor, Horizontal – Option D-15

Indoor, Vertical (by others)

#### Temperature Controls

B-2	Single-Stage Tankstat, 
100-180°F

B-3	2-Stage Tankstat, 100-180°F

B-21	4-Stage TempTracker 
Digital Controller

B-26	2-Stage TempTracker 
Digital Controller

Y-241	Electronic Sequencer, 
1-4 Stages

Y-281	Electronic Sequencer, 
5-8 Stages

#### Additional Safety Controls (Optional)

F-10	Low Water Cut-off, Remote Probe

S-2	Manual High Gas Pressure Switch

#### Regulatory Agency Requirements

C-5	Ignition Lockout Module

#### Other Equipment

Condensing Heat Exchanger

Pump

Soft Water (0-4 grains)

Medium Water (5-15 grains)

Hard Water (16+ grains)

ADB – Type WH

Models 751-1501	Model

Certified Clearances

Front	24” (for service)

Rear	12” (water side)

Right	1”

Left	1”

Top	0” (see note 1)

Floor	0” (see note 2)

Vent	1”

Notes:

1.	24” required for service

2.	DO NOT install on carpeting

| Model | MBTUH |  | B | D | E | F | G | H | K | M | P | Ship Weight | Foot-print | Amps* |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output | Height |  |  |  | NPT | NPT | Flue  |  |  | (Lbs.) | (Ft2) |  |
| WH 751 | 750 | 630 | 64 | 38 | 44-1/2 | 29-3/4 | 1-1/2 | 2 | 8 | 17-3/4 | 41 | 680 | 5.4 | 8 |
| WH 1001 | 999 | 840 | 72 | 46 | 52-1/2 | 37-3/4 | 1-1/2 | 2-1/2 | 10 | 21-1/2 | 49 | 720 | 5.4 | 10 |
| WH 1501 | 1499 | 1260 | 82 | 56 | 62-1/2 | 47-3/4 | 1-1/2 | 2-1/2 | 12 | 20-1/4 | 59 | 780 | 5.4 | 12 |

Dimensions are in inches

* Current draw does NOT include pump.

(Supply breaker must have delayed trip.)

Ratings shown are for elevations up to 5,000 feet. For installations at elevations

over 5,000 feet, please consult the factory for instructions.

NOTE:  For direct vent applications, please contact the factory about relocating the pump.

| ###### Model | ###### RATES OF FLOW AND PRESSURE DROPS |  |  |  |  |  |  |  |  |  |  |  | RECOVERY RATES (GPH) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20ºF T |  | 30ºF T |  | 40ºF T |  | Max. Flow |  |  | Min. Flow |  |  | Temperature Rise at 84% Efficiency |  |  |  |  |  |  |
|  | ###### GPM | P (ft) | ###### GPM | P (ft) | ###### GPM | P (ft) | ###### GPM | P (ft) | ###### T | ###### GPM | P (ft) | ###### T | 20°F | 30°F | 40°F | 50°F | 60°F | 80°F | 100°F |
| WH 751 | 63 | 5.8 | 42 | 2.9 | 32 | 1.8 | 110 | 17.0 | 11°F | 32 | 1.8 | 40°F | 3780 | 2520 | 1890 | 1512 | 1260 | 945 | 756 |
| WH 1001 | 84 | 11.8 | 56 | 5.6 | 42 | 3.4 | 110 | 20.0 | 15°F | 42 | 3.4 | 40°F | 5040 | 3360 | 2520 | 2016 | 1680 | 1260 | 1008 |
| WH 1501 | 126 | 31.4 | 84 | 14.9 | 63 | 9.1 | 126 | 31.4 | 20°F | 63 | 9.1 | 40°F | 7560 | 5040 | 3780 | 3024 | 2490 | 1890 | 1512 |

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com