Proudly Assembled in the USA

Job:

# Hi Delta FlexGas - Type H

## Dual-Fuel Hot Water Boilers 
Models 302BD-902BD

Engineer:

Contractor:

Preparer: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

Fast, Economical Natural-to-Propane Gas Switchover

100% Factory Fire Tested

84% Efficiency

Maximum Outlet Temperature: 230°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Year Thermal Shock Warranty

Diagnostic Center with Fault History

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Patent Nos. 6,904,873 & 7,044,124; other patents pending

Fan-Assisted Low NOx Burners

Patented Burner Security Blanket

#### Heat Exchanger

- H Stamp

- Headers

Glass-Lined Cast Iron – Standard

Bronze – Option A-1

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone High Temp. O-Rings

- ASME Pressure Relief Valve

45 PSIG – Standard on Models  302BD and 402BD

60 PSIG – Standard on Models 502BD-902BD

PSIG – Optional

- Temperature and Pressure Gauge

- Water Connections

Left – Standard

Right – Option A-6

#### Controls

- 120V, 60Hz, 1 Power Supply

- 120/24V 60Hz Transformer

- 100% Shut-Off/Lockout

- Hot Surface Ignition

- Remote Flame Sensor

- High Limit Control, Manual Reset

- On/Off Power Switch

- Manual Shut-Off, Front-Mounted

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switch

- Economaster Pump Time Delay

- Enable/Disable

#### Gas Train

- Manual Gas Shut-Off Valve(s)

- Gas Pressure Regulator

- Safety Shut-Off Valve

- Firing Control Valve

- Firing Mode

On/Off (H8): Models 302BD, 402BD

2-Stage (H9): Models 
302BD-902BD

- Natural/Propane Gas

- Design Certified ANSI Z21.13/
CSA 4.9

- Gas Connection

Left – Standard

Right – Option Z-1

#### Construction

- Indoor/Outdoor Construction

- Enclosed Front Controls

- CSA Low Lead Certified (≤ .25% Lead)

#### Venting

- Vent Location

Top – Standard

Rear – Option D-14

- Vent Termination Cap

Outdoor D-11

Indoor, Horizontal D-15

Indoor, Vertical (by others)

- Combustion Air

In-Line Filter Kit (TruSeal 
only) D-17

Air Intake Elbow D-16

- Extractor – Optional

By others

Not required

#### Burner

- Ultra-Low NOx: Less than 20 PPM (NAT)

#### Temperature Controls

B-6	Aquastat, 2-Stage (100-200°F)

B-  	TempTracker Digital Controller,
2-Stage

B-  	TempTracker Digital Controller,
4-Stage

B-  	TempTracker Mod+ Hybrid (2-16 Boilers)

B-60	Stage Interface

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Start (See 2000.48)

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

For Metric information, see Catalog

#### Regulatory Agency Requirements

For Metric information, see Catalog

#### Hi Delta FlexGas – Type H

#### Models 302BD-902BD 	Model

NOTE: Pump location varies based on model and application

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

SPECIFICATIONS

|  |  |  |  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH |  | A | B | G |  | H | ###### K | T | ###### W | ###### Amp. | Shipping |
| ###### Model | ###### Input | Output | Width |  | ###### Nat | Pro | NPT |  |  |  | ###### Draw* | Wt. (Lbs) |
| 302BD | 300 | 252 | 36 | 41 | 1-1/4 | 3/4 | 2 | 5 | 6 | 18 | 6 | 405 |
| 402BD | 399 | 335 | 43 | 41 | 1-1/4 | 3/4 | 2 | 6 | 6 | 18-1/2 | 6 | 470 |
| 502BD | 500 | 420 | 50 | 35-1/2 | 1-1/4 | 3/4 | 2 | 6 | 6 | 22 | 6 | 570 |
| 652BD | 650 | 546 | 60-1/2 | 30-1/2 | 1-1/4 | 3/4 | 2 | 8 | 6 | 27-1/4 | 6 | 615 |
| 752BD | 750 | 630 | 67-1/2 | 27-1/2 | 1-1/4 | 1-1/4 | 2 | 8 | 6 | 30-3/4 | 6 | 700 |
| 902BD | 900 | 756 | 78 | 34-1/2 | 1-1/4 | 1-1/4 | 2 | 8 | 6 | 36 | 7 | 765 |

* Without pump

NOTES:

1.	Dimensions are in inches

2.	Rates shown are for natural or propane gas, and elevations up to 5,000 feet. For installation above 5,000 feet, please contact manufacturer.

3.	Required natural gas supply pressure is 7 - 10.5” WC. Required propane gas supply pressure is 11 - 13” WC.

RATES OF FLOW AND PRESSURE DROPS

|  | 10°F T |  | 20°F T |  | 30°F T |  | ###### Min. Flow |  |  | ###### Max. Flow |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### Model | ###### GPM | P (ft) | ###### GPM | P (ft) | ###### GPM | P (ft) | ###### GPM | P (ft) | ###### T | ###### GPM | P (ft) | ###### T |
| 302BD | 51 | 3.2 | 25 | <1.0 | N/A | N/A | 20 | <1 | 25 | 90 | 9.8 | 6 |
| 402BD | 68 | 5.4 | 34 | 1.5 | 22 | <1 | 20 | <1 | 34 | 90 | 10.0 | 7 |
| 502BD | 85 | 9.2 | 42 | 2.3 | 28 | 1.1 | 21 | <1 | 40 | 90 | 10.5 | 9 |
| 652BD | N/A | N/A | 55 | 4.0 | 36 | 1.8 | 28 | 1.1 | 40 | 90 | 10.7 | 12 |
| 752BD | N/A | N/A | 64 | 5.5 | 42 | 2.5 | 32 | 1.6 | 40 | 90 | 11.0 | 14 |
| 902BD | N/A | N/A | 76 | 8.5 | 51 | 3.8 | 38 | 2.2 | 40 | 90 | 11.8 | 17 |

Basis is 20 GPM or 40°F T for minimum flow, 90 GPM for maximum flow.