Job:

Engineer:

Contractor:

Preparer: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

Fast, Economical Natural-to-Propane Gas Switchover

100% Factory Fire Tested

84% Efficiency

Maximum Outlet Temperature: 230°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Year Thermal Shock Warranty

Diagnostic Center with Fault History

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-Assisted Low NOx Burners

Patented Burner Security Blanket

#### Heat Exchanger

H Stamp

Headers

Glass-Lined Cast Iron – Standard

Bronze – Option A-1

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone High Temp. O-Rings

ASME Pressure Relief Valve

45 PSIG – Standard on Models  302BD and 402BD

60 PSIG – Standard on Models 502BD-902BD

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

Right – Option A-6

#### Controls

120V, 60Hz, 1( Power Supply

120/24V 60Hz Transformer

100% Shut-Off/Lockout

Hot Surface Ignition

Remote Flame Sensor

High Limit Control, Manual Reset

On/Off Power Switch

Manual Shut-Off, Front-Mounted

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Economaster Pump Time Delay

Enable/Disable

#### Gas Train

Manual Gas Shut-Off Valve(s)

Gas Pressure Regulator

Safety Shut-Off Valve

Firing Control Valve

Firing Mode

On/Off (H8): Models 302BD, 402BD

2-Stage (H9): Models 
302BD-902BD

Natural/Propane Gas

Design Certified ANSI Z21.13/
CSA 4.9

Gas Connection

Left – Standard

Right – Option Z-1

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

CSA Low Lead Certified (≤ .25% Lead)

#### Venting

Vent Location

Top – Standard

Rear – Option D-14

Vent Termination Cap

Outdoor D-11

Indoor, Horizontal D-15

Indoor, Vertical (by others)

Combustion Air

In-Line Filter Kit (TruSeal 
only) D-17

Air Intake Elbow D-16

Extractor – Optional

By others

Not required

#### Burner

Ultra-Low NOx: Less than 20 PPM (NAT)

#### Temperature Controls

B-6	Aquastat, 2-Stage (100-200°F)

B-  	TempTracker Digital Controller,
2-Stage

B-  	TempTracker Digital Controller,
4-Stage

B-  	TempTracker Mod+ Hybrid (2-16 Boilers)

B-60	Stage Interface

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1(, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Start (See 2000.48)

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

#### Regulatory Agency Requirements

#### Hi Delta FlexGas – Type H

#### Models 302BD-902BD 	Model

# Text boxes

Proudly Assembled in the USA

# Hi Delta( FlexGas( - Type H

## Dual-Fuel Hot Water Boilers 
Models 302BD-902BD

Patent Nos. 6,904,873 & 7,044,124; other patents pending

For Metric information, see Catalog

For Metric information, see Catalog

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com

NOTE: Pump location varies based on model and application

NOTES:

1.	Dimensions are in inches

2.	Rates shown are for natural or propane gas, and elevations up to 5,000 feet. For installation above 5,000 feet, please contact manufacturer.

3.	Required natural gas supply pressure is 7 - 10.5” WC. Required propane gas supply pressure is 11 - 13” WC.

SPECIFICATIONS

|  |  |  |  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH | A | B | G | H | K | T | W | Amp. | Shipping |
| Model | Input | Output | Width |  | Nat | Pro | NPT |  |  |  | Draw* | Wt. (Lbs) |
| 302BD | 300 | 252 | 36 | 41 | 1-1/4 | 3/4 | 2 | 5 | 6 | 18 | 6 | 405 |
| 402BD | 399 | 335 | 43 | 41 | 1-1/4 | 3/4 | 2 | 6 | 6 | 18-1/2 | 6 | 470 |
| 502BD | 500 | 420 | 50 | 35-1/2 | 1-1/4 | 3/4 | 2 | 6 | 6 | 22 | 6 | 570 |
| 652BD | 650 | 546 | 60-1/2 | 30-1/2 | 1-1/4 | 3/4 | 2 | 8 | 6 | 27-1/4 | 6 | 615 |
| 752BD | 750 | 630 | 67-1/2 | 27-1/2 | 1-1/4 | 1-1/4 | 2 | 8 | 6 | 30-3/4 | 6 | 700 |
| 902BD | 900 | 756 | 78 | 34-1/2 | 1-1/4 | 1-1/4 | 2 | 8 | 6 | 36 | 7 | 765 |

* Without pump

RATES OF FLOW AND PRESSURE DROPS

|  | 10°F (T | 20°F (T | 30°F (T | Min. Flow | Max. Flow |
| --- | --- | --- | --- | --- | --- |
| Model | GPM | (P (ft) | GPM | (P (ft) | GPM | (P (ft) | GPM | (P (ft) | (T | GPM | (P (ft) | (T |
| 302BD | 51 | 3.2 | 25 | <1.0 | N/A | N/A | 20 | <1 | 25 | 90 | 9.8 | 6 |
| 402BD | 68 | 5.4 | 34 | 1.5 | 22 | <1 | 20 | <1 | 34 | 90 | 10.0 | 7 |
| 502BD | 85 | 9.2 | 42 | 2.3 | 28 | 1.1 | 21 | <1 | 40 | 90 | 10.5 | 9 |
| 652BD | N/A | N/A | 55 | 4.0 | 36 | 1.8 | 28 | 1.1 | 40 | 90 | 10.7 | 12 |
| 752BD | N/A | N/A | 64 | 5.5 | 42 | 2.5 | 32 | 1.6 | 40 | 90 | 11.0 | 14 |
| 902BD | N/A | N/A | 76 | 8.5 | 51 | 3.8 | 38 | 2.2 | 40 | 90 | 11.8 | 17 |

Basis is 20 GPM or 40°F (T for minimum flow, 90 GPM for maximum flow.