Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBH Input:

TruSeal® Direct Vent

Sealed Combustion Chamber

100% Factory Fire Tested

Efficiency: 85%

Maximum Outlet Temperature: 210°F

Minimum Non-condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-year Thermal Shock Warranty

Limited Five-year Heat Exchanger Warranty

Fault Indicator LED

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-assisted

#### Heat Exchanger

HLW Stamp

Headers

Bronze - Standard

Cast Iron, Glass-lined – 
Option A-2

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Finned Tubing

Copper - Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone High Temp O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge

Left-hand Water Connections

#### Controls

120V, 60Hz, 1( Power Supply

120/24V 60Hz Transformer

100% Pilot Shutoff/Lockout

Hot Surface Ignition

Remote Flame Sensor

Fixed High Limit Control, Auto Reset

Fixed High Limit Control, Manual Reset

On/Off Power Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Pump Relay

#### Gas Train

Manual Gas Shut-off Valve(s)

Gas Pressure Regulator

Safety Shut-off Valve

Firing Control Valve

Firing Mode

On/Off (WH1) – Standard

2 Stage (WH3) – Optional

Fuel

Natural Gas

Propane Gas

Design Certified - 
ANSI Z21.10.3/CSA 4.3

#### Construction

Indoor/Outdoor Construction

Front Controls Enclosed

PolyTuf Powder Coat Finish

TruSeal® Direct Vent

Filter Kit

#### Venting

Vent Termination Cap

Outdoor – Option D-11

Indoor, Horizontal – Option D-15

Indoor, Vertical (by others)

Combustion Air

Air Intake Elbow – Option D16

Extractor – Optional

By Others

Not Required

#### Burner

Ultra-Low NOx (<30 ppm)

#### Temperature Controls

B-2	1-Stage Controller, 100-200°F

B-3	2-Stage Controller, 100-200°F

B-  	Remote Controller

By others:

#### Options

F-1	Flow Switch (shipped loose)

F-10	Low Water Cut-off, Remote Probe

I-1	Adjustable High Limit Control, Auto Reset

I-2	Adjustable High Limit Control, Manual Reset

P-  	Pump:      HP, 120V, 160 Hz
 Bronze	 Mounted

Cast Iron	 Loose

X-1	SureRack™ Kit

Two-high

Three-high

#### Hi Delta – Type WH
Models 122-322	Model

RATES OF FLOW AND PRESSURE DROPS

|  | 10ºF (T | 20ºF (T | MIN. FLOW | MAX. FLOW |
| --- | --- | --- | --- | --- |
| MODEL | GPM | (P (ft) | GPM | (P (ft) | GPM | (P (ft) | (T | GPM | (P (ft) | (T |
| WH 122 | 20 | 2.5 | N/A | N/A | 20 | 2.5 | 10 | 30 | 5.4 | 7 |
| WH 162 | 27 | 4.5 | N/A | N/A | 20 | 2.5 | 14 | 30 | 5.5 | 9 |
| WH 202 | 35 | 5.5 | N/A | N/A | 20 | 2.6 | 17 | 35 | 5.5 | 10 |
| WH 242 | 41 | 10.4 | 21 | 2.7 | 20 | 2.7 | 21 | 44 | 11.8 | 9 |
| WH 322 | N/A | N/A | 27 | 4.7 | 20 | 2.7 | 27 | 44 | 12.2 | 12 |

Basis is 20 GPM for minimum flow, 44 GPM for maximum flow (except for 1.25” header).

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 5,000 feet. For installations above 5,000 feet, please contact manufacturer.

2.	Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.

# Text boxes

# Hi Delta® - Type WH

## Water Heaters
Models 122-322

For Metric information, see Catalog

For Metric information, see Catalog

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com

WATER HEATER RECOVERY RATES (GPH)

|  | TEMPERATURE RISE IN ºF |
| --- | --- |
| MODEL | 20º | 30º | 40º | 50º | 60º | 70º | 80º | 90º | 100º |
| WH 122 | 618 | 412 | 309 | 247 | 206 | 177 | 155 | 137 | 124 |
| WH 162 | 824 | 549 | 412 | 330 | 275 | 235 | 206 | 183 | 165 |
| WH 202 | 1030 | 687 | 515 | 412 | 343 | 294 | 258 | 229 | 206 |
| WH 242 | 1236 | 824 | 618 | 495 | 412 | 353 | 309 | 275 | 247 |
| WH 322 | 1648 | 1099 | 824 | 659 | 549 | 471 | 412 | 366 | 330 |

SPECIFICATIONS

|  | MBTUH | FIRING | A | B | H | K | T |
| --- | --- | --- | --- | --- | --- | --- | --- |
| MODEL | INPUT | OUTPUT | STAGES |  |  | NPT |  |  |
| WH 122 | 120 | 102 | 1* | 24-7/8 | 10-3/4 | 1-1/4 | 4 | 5 |
| WH 162 | 160 | 136 | 1* | 28-1/2 | 12-9/16 | 1-1/4 | 5 | 5 |
| WH 202 | 199 | 169 | 1* | 32-1/8 | 14-3/8 | 1-1/4 | 5 | 5 |
| WH 242 | 240 | 204 | 1* | 35-1/2 | 16-3/16 | 1-1/2 | 5 | 5 |
| WH 322 | 320 | 272 | 1* | 42-5/8 | 19-13/16 | 1-1/2 | 6 | 5 |

* 2 stage optional

Dimensions are in inches.

Dimensions are in inches.

Ratings shown for elevation up to 5,000 feet for natural or propane.

For installation at elevations over 5,000 feet, please contact manufacturer.

Ratings based on natural gas or propane.

Natural gas pressure recommended to be between 7 & 14” w.c.

Propane gas pressure recommended to be between 11 & 14” w.c.

###### BOILER RATE OF FLOW AND PRESSURE DROP

|  | 20°F (T | Max. Flow | Min. Flow |
| --- | --- | --- | --- |
| Model | GPM | (P (ft) | GPM | (P (ft) | (T | GPM | (P (ft) | (T |
| 122 | N/A | N/A | 44 | 11.2 | 5 | 20 | 2.50 | 10 |
| 162 | N/A | N/A | 44 | 11.4 | 6 | 20 | 2.55 | 14 |
| 202 | N/A | N/A | 44 | 11.6 | 8 | 20 | 2.60 | 17 |
| 242 | 21 | 2.95 | 44 | 11.8 | 9 | 20 | 2.65 | 21 |
| 322 | 27 | 4.7 | 44 | 12.2 | 12 | 20 | 2.75 | 27 |

###### DIMENSIONAL DATA

|  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH |  | A | G | H | K | T | Amp. | Shipping |
| Model | Input | Output | Width | NPT | NPT |  |  | Draw | Wt. (Lbs) |
| 122 | 120 | 102 | 24.9 | 3/4 | 1-1/4 | 4 |  | < 5.0 |  |
| 162 | 160 | 136 | 28.5 | 3/4 | 1-1/4 | 4 |  | < 5.0 |  |
| 202 | 199 | 169 | 32.1 | 3/4 | 1-1/4 | 4 |  | < 5.0 |  |
| 242 | 240 | 204 | 35.0 | 3/4 | 1-1/2 | 5 |  | < 5.0 |  |
| 322 | 320 | 272 | 42.6 | 3/4 | 1-1/2 | 5 |  | < 5.0 |  |