Job:

# Hi Delta® - Type WH

## Water Heaters
Models 122-322

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBH Input:

TruSeal® Direct Vent

Sealed Combustion Chamber

100% Factory Fire Tested

Efficiency: 85%

Maximum Outlet Temperature: 210°F

Minimum Non-condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-year Thermal Shock Warranty

Limited Five-year Heat Exchanger Warranty

Fault Indicator LED

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-assisted

#### Heat Exchanger

- HLW Stamp

- Headers

Bronze - Standard

Cast Iron, Glass-lined – 
Option A-2

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Finned Tubing

Copper - Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone High Temp O-Rings

- ASME Pressure Relief Valve

125 PSIG – Standard

PSIG – Optional

- Temperature and Pressure Gauge

- Left-hand Water Connections

#### Controls

- 120V, 60Hz, 1 Power Supply

- 120/24V 60Hz Transformer

- 100% Pilot Shutoff/Lockout

- Hot Surface Ignition

- Remote Flame Sensor

- Fixed High Limit Control, Auto Reset

- Fixed High Limit Control, Manual Reset

- On/Off Power Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switch

- Pump Relay

#### Gas Train

- Manual Gas Shut-off Valve(s)

- Gas Pressure Regulator

- Safety Shut-off Valve

- Firing Control Valve

- Firing Mode

On/Off (WH1) – Standard

2 Stage (WH3) – Optional

- Fuel

Natural Gas

Propane Gas

- Design Certified - 
ANSI Z21.10.3/CSA 4.3

#### Construction

- Indoor/Outdoor Construction

- Front Controls Enclosed

- PolyTuf Powder Coat Finish

- TruSeal® Direct Vent

- Filter Kit

#### Venting

- Vent Termination Cap

Outdoor – Option D-11

Indoor, Horizontal – Option D-15

Indoor, Vertical (by others)

- Combustion Air

Air Intake Elbow – Option D16

- Extractor – Optional

By Others

Not Required

#### Burner

- Ultra-Low NOx (<30 ppm)

#### Temperature Controls

B-2	1-Stage Controller, 100-200°F

B-3	2-Stage Controller, 100-200°F

B-  	Remote Controller

By others:

#### Options

F-1	Flow Switch (shipped loose)

F-10	Low Water Cut-off, Remote Probe

I-1	Adjustable High Limit Control, Auto Reset

I-2	Adjustable High Limit Control, Manual Reset

P-  	Pump:      HP, 120V, 160 Hz
 Bronze	 Mounted

Cast Iron	 Loose

X-1	SureRack™ Kit

Two-high

Three-high

For Metric information, see Catalog

For Metric information, see Catalog

#### Hi Delta – Type WH
Models 122-322	Model

WATER HEATER RECOVERY RATES (GPH)

|  | TEMPERATURE RISE IN ºF |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MODEL | 20º | 30º | 40º | 50º | 60º | 70º | 80º | 90º | 100º |
| WH 122 | 618 | 412 | 309 | 247 | 206 | 177 | 155 | 137 | 124 |
| WH 162 | 824 | 549 | 412 | 330 | 275 | 235 | 206 | 183 | 165 |
| WH 202 | 1030 | 687 | 515 | 412 | 343 | 294 | 258 | 229 | 206 |
| WH 242 | 1236 | 824 | 618 | 495 | 412 | 353 | 309 | 275 | 247 |
| WH 322 | 1648 | 1099 | 824 | 659 | 549 | 471 | 412 | 366 | 330 |

SPECIFICATIONS

|  | MBTUH |  | FIRING | A | B | H | K | T |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MODEL | INPUT | OUTPUT | STAGES |  |  | NPT |  |  |
| WH 122 | 120 | 102 | 1* | 24-7/8 | 10-3/4 | 1-1/4 | 4 | 5 |
| WH 162 | 160 | 136 | 1* | 28-1/2 | 12-9/16 | 1-1/4 | 5 | 5 |
| WH 202 | 199 | 169 | 1* | 32-1/8 | 14-3/8 | 1-1/4 | 5 | 5 |
| WH 242 | 240 | 204 | 1* | 35-1/2 | 16-3/16 | 1-1/2 | 5 | 5 |
| WH 322 | 320 | 272 | 1* | 42-5/8 | 19-13/16 | 1-1/2 | 6 | 5 |

* 2 stage optional

Dimensions are in inches.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

RATES OF FLOW AND PRESSURE DROPS

|  | 10ºF T |  | 20ºF T |  | MIN. FLOW |  |  | MAX. FLOW |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MODEL | GPM | P (ft) | GPM | P (ft) | GPM | P (ft) | T | GPM | P (ft) | T |
| WH 122 | 20 | 2.5 | N/A | N/A | 20 | 2.5 | 10 | 30 | 5.4 | 7 |
| WH 162 | 27 | 4.5 | N/A | N/A | 20 | 2.5 | 14 | 30 | 5.5 | 9 |
| WH 202 | 35 | 5.5 | N/A | N/A | 20 | 2.6 | 17 | 35 | 5.5 | 10 |
| WH 242 | 41 | 10.4 | 21 | 2.7 | 20 | 2.7 | 21 | 44 | 11.8 | 9 |
| WH 322 | N/A | N/A | 27 | 4.7 | 20 | 2.7 | 27 | 44 | 12.2 | 12 |

Basis is 20 GPM for minimum flow, 44 GPM for maximum flow (except for 1.25” header).

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 5,000 feet. For installations above 5,000 feet, please contact manufacturer.

2.	Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.

Dimensions are in inches.

Ratings shown for elevation up to 5,000 feet for natural or propane.

For installation at elevations over 5,000 feet, please contact manufacturer.

Ratings based on natural gas or propane.

Natural gas pressure recommended to be between 7 & 14” w.c.

Propane gas pressure recommended to be between 11 & 14” w.c.

###### DIMENSIONAL DATA

|  |  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH |  |  | A | G | H | K | T | ###### Amp. | Shipping |
| ###### Model | ###### Input | Output |  | Width | ###### NPT | NPT |  |  | ###### Draw | Wt. (Lbs) |
| 122 | 120 | 102 |  | 24.9 | 3/4 | 1-1/4 | 4 |  | < 5.0 |  |
| 162 | 160 | 136 |  | 28.5 | 3/4 | 1-1/4 | 4 |  | < 5.0 |  |
| 202 | 199 | 169 |  | 32.1 | 3/4 | 1-1/4 | 4 |  | < 5.0 |  |
| 242 | 240 | 204 |  | 35.0 | 3/4 | 1-1/2 | 5 |  | < 5.0 |  |
| 322 | 320 | 272 |  | 42.6 | 3/4 | 1-1/2 | 5 |  | < 5.0 |  |

###### BOILER RATE OF FLOW AND PRESSURE DROP

|  | 20°F T |  | Max. Flow |  |  | Min. Flow |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### Model | ###### GPM | P (ft) | ###### GPM | P (ft) | ###### T | ###### GPM | P (ft) | ###### T |
| 122 | N/A | N/A | 44 | 11.2 | 5 | 20 | 2.50 | 10 |
| 162 | N/A | N/A | 44 | 11.4 | 6 | 20 | 2.55 | 14 |
| 202 | N/A | N/A | 44 | 11.6 | 8 | 20 | 2.60 | 17 |
| 242 | 21 | 2.95 | 44 | 11.8 | 9 | 20 | 2.65 | 21 |
| 322 | 27 | 4.7 | 44 | 12.2 | 12 | 20 | 2.75 | 27 |