# Delta Limited® - Type WH

## Water Heaters
Models 399B-899B

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

100% Factory Fire Tested

Efficiency: Up to 85%

Maximum Setpoint: 150°F

Maximum Outlet Temperature: 200°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Year Thermal Shock Warranty

Shown with outdoor 
air inlet and pump covers

Limited Ten-Year Cupro-Nickel Heat Exchanger Warranty

Limited Five-Year Copper Heat Exchanger Warranty

PolyTuf Powder Coated Cabinet

Combustible Floor Shield Required

Fan-Assisted

Proudly Assembled in the U.S.A.

Patented Burner Security Blanket

#### Heat Exchanger

ASME HLW Stamp

Headers

Glass-Lined Cast Iron – Standard

A-1 Bronze

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper (Std.) 85%

Cupro-Nickel 83.1%

ASME Steel Tube Sheet

Silicone High Temp O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

A-6 Right

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

100% Shut-Off/Lockout

Hot Surface Ignition

Ignition Module

- 3-Try Standard

- C-6 Single-Try

Remote Flame Sensor

High Limit Control, Manual Reset

On/Off Power Switch

Manual Shut-Off, Front-Mounted Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Pump Time Delay Relay, 5 Minute, Fixed

Status Display Lights

#### Gas Train

Manual Gas Shut-Off Valve(s)

Combination Valves

Firing Mode

On/Off: Model 399B

2 Stage: Models 499B-899B

Fuel

Natural Gas

Propane Gas

Design Certified – 
ANSI Z21.10.3/CSA 4.3

#### Burner

Ultra-Low NOx:
Less 	than 20 PPM

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

CSA Low Lead Certified ≤ 0.25% Lead

#### Venting

Vent Category I/III Cupro-Nickel

Vent Category II/IV Copper

Vent Location

Top, Outdoor – Standard

D-20 Top, Indoor

D-14 Rear

Vent Termination Cap

D-11 Outdoor

D-15 Horizontal

Indoor, Vertical (by others)

Extractor – Optional

By others

Not required

Delta Limited models not approved for use in California

Temperature Controls

B-2	Tankstat, Single-Stage 
(100-200°F)

B-3	Tankstat, 2-Stage (100-200°F)

B-__	TempTracker Digital Controller,   2-Stage (Loose)

B-__	TempTracker Digital Controller,    4-Stage (Loose)

#### Options

C-6	Ignition Module, Manual Reset

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1, 60Hz 
Water Hardness:       GPG

Bronze
 Mounted	 Loose

Front	 Rear

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack  Kit

X-2	SureRack Add-on

For Metric information, see Catalog

#### Regulatory Agency Requirements

For Metric information, see Catalog

For Metric information, see Catalog

#### Delta Limited – Type WH
Models 399B-899B                                                                     Model

NOTE: Pump location varies based on model selected

Raypak, Inc.  2151 Eastman Avenue, Oxnard, CA  93030  (805) 278-5300  Fax (800) 872-9725  www.raypak.com

| Model | SPECIFICATIONS |  |  |  |  |  |  |  | Approx. Shipping Wt. (lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH |  |  | A Width | G NPT | K | W | Amp. Draw |  |
|  | Input | Output 85% | Output 83.1% |  |  |  |  |  |  |
| 399B | 399 | 339 | 332 | 43 | 3/4 | 6 | 18-1/2 | 6 | 445 |
| 499B | 500 | 425 | 416 | 50 | 1-1/4 | 6 | 22 | 6 | 545 |
| 649B | 650 | 553 | 540 | 60-1/2 | 1-1/4 | 8 | 27-1/4 | 6 | 590 |
| 749B | 750 | 638 | 623 | 67-1/2 | 1-1/4 | 8 | 30-3/4 | 6 | 675 |
| 899B | 900 | 765 | 748 | 78 | 1-1/4 | 8 | 36 | 7 | 740 |

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

2.	Recommended natural gas supply pressure is 7 – 10.5” WC. Recommended propane gas supply pressure is 11 - 13” WC.

3.	Amp draw is heater less pump

#### Delta Limited – Type WH
Models 399B-899B                                                                     Model

| Model | 83.1% System Flow and Head Loss |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25** Grains Per Gallon |  |  |  |  |
|  | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) |
| 399B | 17 | 40 | 2.0 | 2 | 5.1 | 13 | 52 | 3.4 | 2 | 8.4 | 7 | 90 | 10.0 | 2 | 23.8 |
| 499B | 21 | 40 | 2.1 | 2 | 5.2 | 16 | 52 | 3.5 | 2 | 8.6 | 9 | 90 | 10.4 | 2 | 24.2 |
| 649B | 27 | 40 | 2.2 | 2 | 5.3 | 21 | 52 | 3.7 | 2 | 8.7 | 12 | 90 | 10.8 | 2 | 24.7 |
| 749B | 28 | 45 | 3.0 | 2 | 6.8 | 23 | 55 | 4.4 | 2 | 9.9 | 14 | 90 | 11.3 | 2 | 25.1 |
| 899B | 28 | 54 | 4.3 | 2 | 9.7 | 21 | 73 | 7.8 | 2 | 17.2 | 17 | 90 | 11.7 | 2 | 25.5 |

| Model | 85% System Flow and Head Loss |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25** Grains Per Gallon |  |  |  |  |
|  | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) |
| 399B | 17 | 40 | 2.0 | 2 | 5.1 | 13 | 52 | 3.4 | 2 | 8.4 | 8 | 90 | 10.0 | 2 | 23.8 |
| 499B | 21 | 40 | 2.1 | 2 | 5.2 | 17 | 52 | 3.5 | 2 | 8.6 | 10 | 90 | 10.4 | 2 | 24.2 |
| 649B | 28 | 40 | 2.2 | 2 | 5.3 | 21 | 52 | 3.7 | 2 | 8.7 | 12 | 90 | 10.8 | 2 | 24.7 |
| 749B | 29 | 45 | 3.0 | 2 | 6.8 | 23 | 55 | 4.4 | 2 | 9.9 | 14 | 90 | 11.3 | 2 | 25.1 |
| 899B | 29 | 54 | 4.3 | 2 | 9.7 | 21 | 73 | 7.8 | 2 | 17.2 | 17 | 90 | 11.7 | 2 | 25.5 |

SHL includes 50 ft of tubing each way (100 total)

** Must use optional cupro-nickel tubes. For hardness exceeding 25 GPG, must use water softener

Basis for minimum flow is 40 GPM or 30°F ∆T, 90 GPM for maximum flow

| Model | 83.1 % Recovery Rates |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 100° |
| 399B | 2010 | 1340 | 1005 | 804 | 670 | 574 | 502 | 447 | 402 |
| 499B | 2518 | 1679 | 1259 | 1007 | 839 | 709 | 630 | 560 | 504 |
| 649B | 3274 | 2182 | 1637 | 1309 | 1091 | 935 | 818 | 727 | 655 |
| 749B | 3777 | 2518 | 1889 | 1511 | 1259 | 1079 | 944 | 839 | 755 |
| 899B | 4533 | 3022 | 2266 | 1813 | 1511 | 1295 | 1133 | 1007 | 907 |

| Model | 85 % Recovery Rates |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 100° |
| 399B | 2055 | 1370 | 1028 | 822 | 685 | 587 | 514 | 457 | 411 |
| 499B | 2576 | 1717 | 1288 | 1030 | 859 | 736 | 644 | 572 | 515 |
| 649B | 3348 | 2232 | 1674 | 1339 | 1116 | 957 | 837 | 744 | 670 |
| 749B | 3864 | 2576 | 1932 | 1545 | 1288 | 1104 | 966 | 859 | 773 |
| 899B | 4636 | 3091 | 2318 | 1855 | 1545 | 1325 | 1159 | 1030 | 927 |

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com