Job:

# Hi Delta® - Type WH

## Water Heaters
Models 302B-902B

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

100% Factory Fire Tested

Patent No. 7,044,124

Efficiency: 85%

Maximum Outlet Temperature: 200°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Five-Year Thermal Shock Warranty

Limited Five-Year Heat Exchanger Warranty

Full Safety Diagnostics with Fault History

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-Assisted

Proudly Assembled in the USA

Patented Burner Security Blanket

#### Heat Exchanger

- HLW Stamp

- Headers

Brass – Standard

Glass-Lined Cast Iron – 
Option A-2

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone High Temp. O-Rings

- ASME Pressure Relief Valve

125 PSIG – Standard

PSIG – Optional

- Temperature and Pressure Gauge

- Water Connections

Left – Standard

Right – Option A-6

#### Controls

- 120V, 60Hz, 1 Power Supply

- 120/24V 60Hz Transformer

- 100% Shut-Off/Lockout

- Hot Surface Ignition

- Remote Flame Sensor

- High Limit Control, Manual Reset

- On/Off Power Switch

- Manual Shut-Off, Front-Mounted

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switch

- Economaster Style Pump Time Delay

- Enable/Disable

- Diagnostic Panel with LCD Display 2 Lines, 20 Characters

#### Gas Train

- Manual Gas Shut-Off Valve(s)

- Combo Valve(s)

- Firing Mode

On/Off: Models 302B-402B

2-Stage: Models 302B-902B

- Fuel

Natural Gas

Propane Gas

4” WC Gas Supply Pressure 
G-20

- Design Certified - ANSI Z21.10.3/
CSA 4.3

#### Construction

- Indoor/Outdoor Construction

- Front Controls Enclosed

- PolyTuf Powder Coat Finish

- CSA Low Lead Certified ≤ .25% Lead

#### Venting

- Vent Location

Top – Standard

Rear – Option D-14

- Vent Termination Cap

Outdoor  D-11

Indoor, Horizontal  D-15

Indoor, Vertical (by others)

- Combustion Air

In-Line Filter Kit (TruSeal 
only)  D-17

Air Intake Elbow  D-16

- Extractor – Optional

By others

Not required

#### Burner

#### Ultra-Low NOx: Less than 20 PPM

#### Temperature Controls

B-2	Tankstat, Single-Stage 
(100-200°F)

B-3	Tankstat, 2-Stage (100-200°F)

B-21	TempTracker Digital Controller, 
4-Stage

B-25	Raytemp Digital Controller, 
4-Stage

B-  	TempTracker MOD+ Hybrid (Up to 16 heaters)

B-60	Stage Interface Card

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1, 60Hz Water Hardness:       GPG

Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Run (See 1000.19)

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

#### Regulatory Agency Requirements

#### Hi Delta – Type WH
Models 302B-902B	Model

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

2.	Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.

###### RECOVERY RATES (GPH)

|  | Temperature Rise in °F |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### Model | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 100° |
| 302B | 1545 | 1030 | 773 | 618 | 515 | 442 | 386 | 343 | 309 |
| 402B | 2055 | 1370 | 1028 | 822 | 685 | 587 | 514 | 457 | 411 |
| 502B | 2576 | 1717 | 1288 | 1030 | 859 | 736 | 644 | 572 | 515 |
| 652B | 3348 | 2232 | 1674 | 1339 | 1116 | 957 | 837 | 744 | 670 |
| 752B | 3864 | 2576 | 1932 | 1545 | 1288 | 1104 | 966 | 859 | 773 |
| 902B | 4636 | 3091 | 2318 | 1855 | 1545 | 1325 | 1159 | 1030 | 927 |

SPECIFICATIONS

|  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH |  | A | G | K | ###### W | ###### Amp. | Shipping |
| ###### Model | ###### Input | Output | Width | NPT |  |  | ###### Draw | Wt. (Lbs) |
| 302B | 300 | 255 | 36 | 3/4 | 5 | 18 | 6 | 380 |
| 402B | 399 | 339 | 43 | 3/4 | 6 | 18-1/2 | 6 | 445 |
| 502B | 500 | 425 | 50 | 1-1/4 | 6 | 22 | 6 | 545 |
| 652B | 650 | 553 | 60-1/2 | 1-1/4 | 8 | 27-1/4 | 6 | 590 |
| 752B | 750 | 638 | 67-1/2 | 1-1/4 | 8 | 30-3/4 | 6 | 675 |
| 902B | 900 | 765 | 78 | 1-1/4 | 8 | 36 | 7 | 740 |

Dimensions are in inches.

NOTE:  Pump location varies based on model and application.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

| Model | System Flow and Head Loss |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25** Grains Per Gallon |  |  |  |  |
|  | ∆T (ºF) | GPM | ∆P (ft wc) | MTS (in) | SHL (ft wc) | ∆T (ºF) | GPM | ∆P (ft wc) | MTS (in) | SHL (ft wc) | ∆T (ºF) | GPM | ∆P (ft wc) | MTS (in) | SHL (ft wc) |
| 302B | 13 | 40 | 2.0 | 2 | 5.1 | 10 | 52 | 3.3 | 2 | 8.3 | 7 | 74 | 6.6 | 2 | 16.3 |
| 402B | 17 | 40 | 2.0 | 2 | 5.1 | 13 | 52 | 3.4 | 2 | 8.4 | 9 | 74 | 6.8 | 2 | 16.4 |
| 502B | 21 | 40 | 2.1 | 2 | 5.2 | 16 | 52 | 3.5 | 2 | 8.6 | 12 | 73 | 6.9 | 2 | 16.3 |
| 652B | 28 | 40 | 2.2 | 2 | 5.3 | 20 | 55 | 4.1 | 2 | 9.7 | 15 | 72 | 7.0 | 2 | 16.2 |
| 752B | 30 | 42 | 2.6 | 2 | 6.0 | 17 | 73 | 7.5 | 2 | 16.9 | 14 | 90 | 11.3 | 2 | 25.1 |
| 902B | 30 | 51 | 3.9 | 2 | 8.7 | 21 | 73 | 7.8 | 2 | 17.2 | 17 | 90 | 11.7 | 2 | 25.5 |

SHL includes 50 ft of tubing each way (100 total)

** Must use optional cupro-nickel tubes. For hardness exceeding 25 GPG, must use water softener