# Hi Delta - Type H

## Space Heating/Hot Water Boilers Models 992C-2342C

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

- 100% Factory Fire Tested

- Thermal Efficiency: 84%

- Versa IC® Controller with LCD Display

- Maximum Setpoint: 220°F

- Maximum Outlet Temperature: 240°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal Shock Proof Heat Exchanger

- Limited Twenty-Year Thermal Shock Warranty

- Limited Five-Year Heat Exchanger Warranty

- Full Safety Diagnostics with Fault History

- PolyTuf Powder Coated Cabinet

- No Combustible Floor Shield Required

- Fan-Assisted

Proudly Assembled in the USA

Patented Burner Security Blanket

- Cascade up to 4 Heaters – No External Sequencer Needed

- Ultra-Low NOx – SCAQMD 1146.2 Certified (992C – 2002C)

#### Heat Exchanger

Headers

Glass-Lined Cast Iron – Standard

A-1 Brass

ASME Inspected and H Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper – Standard

A-3 Cupro Nickel

ASME Steel Tube Sheet

Silicone High Temp. O-Rings

ASME Pressure Relief Valve

60 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

A-6 Right

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

Versa IC® Integrated Control

100% Shut-Off/Lockout

Hot Surface Ignition

Ignition Module

- 3-Try – Standard

- C-6 Single Try

Remote Flame Sensor

Fixed High Limit, Manual Reset 240°F

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Programmable Pump Time Delays

Pump Outputs

Boiler

System – Pilot Duty

DHW Indirect – Pilot Duty

Enable/Disable

LCD Display; Status, Fault and Diagnostics

Modbus RTU BMS Port (Up to 115K Baud,   See Cat. 5000.73)

- B-85 – BMS Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

- B-86 – BMS Gateway – LonWorks

Cold Water Protection Function

- CWR Variable-Speed Pump

- CWS Proportional Valve

#### Gas Train

Manual Gas Shut-Off Valve(s)

Combo Valve(s)

Firing Mode

3-Stage (H8): Model 992C

4-Stage (H9): Models 1262C – 2342C

Fuel

Natural Gas

Propane Gas (HD-5) (Excludes 2002C)

4” WC Nat Supply Pressure 
(G-20)

Design Certified - ANSI Z21.13/CSA 4.9

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

- CSA Low Lead Certified (≤ .25% Lead

#### Venting

Vent Location

Top – Standard

D-14 Rear

Vent Termination Cap

D-11 Outdoor

D-15 Indoor, Horizontal

Indoor, Vertical (by others)

Combustion Air

D-17 In-Line Filter Kit (TruSeal only)

D-16 Air Intake Elbow

Extractor – Optional

By others

Not required

#### Burner

#### Ultra-Low NOx: Less than 20 PPM

#### Options

D-21	TruSeal Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset (240°F)

I-2	Adjustable High Limit Control, Manual Reset (240°F)

P-  	Pump:       HP, 120V, 1, 60Hz

Bronze	 Cast Iron
 Mounted	 Loose

Front	 Rear

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack® Kit

X-2	SureRack Add-on

For Metric information, see Catalog

#### Additional Options or Accessories

For Metric information, see Catalog

#### Multi-Boiler Temperature Controllers

TempTracker Mod+ Hybrid

B-36, 2-4 Heaters

B-37, 5-10 Heaters

B-38, 11-16 Heaters

B-39 EMS 4-20mA Remote Setpoint Interface Module

B-62 BACnet MS/TP Interface

#### Hi Delta – Type H

Models 992C-2342C	Model

NOTE:  Pump location varies based on model and application

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

|  | RATES OF FLOW AND PRESSURE DROPS |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | 20°F ΔT |  | 30°F ΔT |  | Min. Flow |  |  | Max. Flow |  |  |
|  | GPM | ΔP (FT.) | GPM | ΔP (FT.) | GPM | ΔP (FT.) | ΔT | GPM | ΔP (FT.) | ΔT |
| 992C | 84 | 5.6 | 56 | 2.5 | 43 | 1.5 | 39 | 132 | 14.0 | 13 |
| 1262C | 107 | 10.0 | 71 | 4.5 | 54 | 2.6 | 39 | 132 | 15.5 | 16 |
| 1532C | 130 | 16.0 | 86 | 7.1 | 66 | 4.1 | 39 | 132 | 16.5 | 20 |
| 1802C | N/A | N/A | 102 | 10.8 | 78 | 6.0 | 39 | 132 | 18.0 | 23 |
| 2002C | N/A | N/A | 113 | 14.0 | 86 | 8.1 | 39 | 132 | 19.5 | 26 |
| 2072C | N/A | N/A | 117 | 15.0 | 89 | 8.7 | 39 | 132 | 19.5 | 27 |
| 2342C | N/A | N/A | 132 | 21.0 | 101 | 12.0 | 39 | 132 | 21.0 | 30 |

Basis is 39°F ΔT for minimum flow, 132 GPM for maximum flow.

| SPECIFICATIONS |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model |  |  | Firing Stages | A Width | K | T | W | Amp. Draw* | Approx. Shipping Wt. (Lbs.) |
|  | Input | Output |  |  |  |  |  |  |  |
| 992C | 990 | 832 | 3 | 57-1/8 | 10 | 10 | 16-13/16 | <12 | 900 |
| 1262C | 1260 | 1058 | 4 | 68-1/2 | 12 | 10 | 20-9/16 | <12 | 1010 |
| 1532C | 1530 | 1285 | 4 | 79-7/8 | 12 | 10 | 24-3/8 | <12 | 1225 |
| 1802C | 1800 | 1512 | 4 | 91-1/8 | 14 | 10 | 28-1/8 | <12 | 1350 |
| 2002C | 1999 | 1679 | 4 | 102-1/2 | 14 | 10 | 31-15/16 | <12 | 1450 |
| 2072C | 2070 | 1739 | 4 | 102-1/2 | 14 | 10 | 31-15/16 | <12 | 1450 |
| 2342C | 2340 | 1966 | 4 | 113-7/8 | 16 | 10 | 35-11/16 | <12 | 1520 |

*Without pump.

Dimensions are in inches.

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

2.	Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.