Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

Stainless Steel Water-tube Construction

95% Thermal Efficiency at Full Rate

VERSA IC® Modulating Controller

LCD Status Display with Full Diagnostics and Fault Memory

Cascade up to Four Heaters – No External Sequencer Required

Modbus RTU BMS Port

Soft Start, Electronic Modulation, 5:1 Turndown

Maximum Outlet Water Temperature: 175°F

Maximum Setpoint: 150°F

100% Factory Fire Tested

Zero Clearance to Combustibles

Indoor/Outdoor Construction Standard

PVC, CPVC, Centrotherm™ Polypropylene or Stainless Venting Certified1

Meets 2012 NOx Requirements (< 20 ppm)

Limited Twenty-Five-Year Thermal Shock Warranty

Limited Ten-Year Heat Exchanger Warranty

#### Heat Exchanger

All Stainless Steel Construction with Copper Connections

Gasketless Heat Exchanger Design

ASME H Stamped
160 PSIG Max Working Pressure

National Board Approved

ASME Pressure Relief Valve, Loose

125 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge,
Shipped Loose

#### Control

120V, 60Hz, 1Ø, Power Supply

VERSA IC Operating Control with LCD display

0-10 VDC input for BMS

Cascade up to 4 water heaters

Remote Flame Sensor

High Limit, Manual Reset, Fixed, 175ºF

Alarm Dry Contact Connection

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Boiler, DHW & System Pump Contacts

Water Temperature Sensors (3)10kΩ (Tank sensor shipped loose)

#### Burner

Spark Ignition (DSI)

Ultra-Low NOx: Less than 20 PPM

#### Gas Train

Fuel

Natural Gas

Propane

Dual-Seat Combination Valve

Electronic Modulating Firing Mode (WH7)

#### Construction

Indoor/Outdoor Construction

Front Controls Enclosed

PolyTuf Powder Coat Finish

Rear Connections (Electrical, Gas, Vent, Combustion Air)

Top Connections (Water)

Design Certified ANSI Z21.10.3/
CSA 4.3

Combustion Air Filter

Condensate Trap

CSA Low Lead Certified ≤ .25% Lead

#### Venting (PVC -CPVC- Centrotherm™ Polypropylene-Stainless) 1

Vent Termination

D-15     Indoor, Horizontal – Option

D-11     Outdoor Termination

D-33     Polypropylene Adapter

Extractor – Optional

By others

Not required

#### Options

D-21 	TruSeal® Combustion Air Inlet (Mounted)

D-22 	TruSeal® Combustion Air Inlet (Loose)

F-10 	Low Water Cut-Off, Remote Probe

P-  	Pump:      HP, 120V,	1(, 60Hz

Bronze/SS

S-1/S-2  High/Low Gas Pressure

Switches, Manual Reset

Z-12	Condensate Neutralizer Kit

#### Regulatory Agency Requirements

XFyre – Type WH

Models 300A-850A	Model

| Model (H7-) | MBTUH | Dimensions (in.) |
| --- | --- | --- |
|  | Input | Output | A Length | F Mounting | G NPT | H NPT | K Flue Ø | T C/A Ø | W (Water) |
| 300A | 300 | 282 | 28-1/4 | 27-9/16 | 3/4 | 1-1/2 | 4 | 4 | 8-1/2 |
| 400A | 399 | 375 | 30-3/4 | 32-5/16 | 1 | 2 | 4 | 4 | 7 |
| 500A | 500 | 470 | 37-1/4 | 36-9/16 | 1 | 2 | 4 | 4 | 8-1/2 |
| 700A | 700 | 658 | 47-3/4 | 49-5/16 | 1-1/4 | 2 | 6 | 6 | 10-5/8 |
| 850A | 850 | 799 | 54-1/4 | 53-9/16 | 1-1/4 | 2 | 6 | 6 | 10-5/8 |

|  | CLEARANCES (in.) |
| --- | --- |
|  | Certified Minimum | Service Clearance |
| Front | 24 | 24 |
| Rear | 24 | 24 |
| Right | 0 | 0 |
| Left | 0 | 0 |
| Top | 12 | 24 |
| Floor | 0 | - |
| Vent | 1 | - |

| Model (H7-) | Amps* | Foot- Print (ft2) | Ship Weight (lbs.) |
| --- | --- | --- | --- |
| 300A | 3 | 4.3 | 410 |
| 400A | 4 | 4.7 | 465 |
| 500A | 4 | 5.7 | 505 |
| 700A | 5 | 7.3 | 580 |
| 850A | 5 | 8.3 | 580 |

| Model (WH7-) | 3-15 grains per gallon | Hard (16-25 grains per gallon) |
| --- | --- | --- |
|  | ∆T | GPM | ∆P | MTS | SHL | Do not use when hardness exceeds 15 grains per gallon |
| 300A | 24 | 24 | 12 | 1.5 | 17 |  |
| 400A | 20 | 38 | 18 | 2 | 20 |  |
| 500A | 20 | 48 | 16 | 2 | 19 |  |
| 700A | 20 | 67 | 30 | 2 | 36 |  |
| 850A | 23 | 70 | 30 | 2 | 36 |  |

* Current draw is for heater only.

(Supply breaker must have delayed trip.)

MTS = Minimum Tube Size, inch

SHL = System head loss, ft (based on heater and tank placed no more than 5ft apart & 75ft equivalent length of tubing and fittings).

ΔT = Temperature rise, °F

ΔP = Pressure drop through heat exchanger, ft

XFyre – Type WH

Models 300A-850A	Model

| Model (WH7-) | Recovery Rates (gallons per hour) |
| --- | --- |
|  | Temperature Rise (ºF) |
|  | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |
| 300 | 1728 | 1151 | 863 | 691 | 576 | 494 | 432 | 384 | 345 |
| 400 | 2297 | 1532 | 1149 | 919 | 765 | 656 | 575 | 511 | 459 |
| 500 | 2879 | 1919 | 1440 | 1151 | 959 | 823 | 720 | 640 | 576 |
| 700 | 4031 | 2687 | 2015 | 1612 | 1344 | 1151 | 1008 | 986 | 806 |
| 850 | 4894 | 3262 | 2446 | 1958 | 1632 | 1398 | 1224 | 1087 | 978 |

# Text boxes

# XFyre® - Type WH

Condensing Water Heaters
Models 300A-850A

Proudly Assembled in the USA

Note 1: Configured for PVC Vent Standard. Maximum Return Water Temperature of 130°F on models WH7-700A and WH7-850A for PVC Vent.

See I & O Manual Cat. 1000.65

2-3/4

Ratings shown are for elevations up to 2,000 feet. For installations at elevations above 2,000, please consult the factory for additional instructions.

|  | CLEARANCES (in.) |
| --- | --- |
|  | Certified Minimum | Service Minimum |
| Front | 24 | 24 |
| Rear | 24 | 24 |
| Right | 0 | 0 |
| Left | 0 | 0 |
| Top | 12 | 24 |
| Floor | 0 | -- |
| Vent | 1 | -- |

|  | CLEARANCES (in.) |
| --- | --- |
|  | Certified Minimum | Service Minimum |
| Front | 24 | 24 |
| Rear | 24 | 24 |
| Right | 0 | 0 |
| Left | 0 | 0 |
| Top | 12 | 24 |
| Floor | 0 | -- |
| Vent | 1 | -- |

|  | CLEARANCES (in.) |
| --- | --- |
|  | Certified Minimum | Service Minimum |
| Front | 24 | 24 |
| Rear | 24 | 24 |
| Right | 0 | 0 |
| Left | 0 | 0 |
| Top | 12 | 24 |
| Floor | 0 | -- |
| Vent | 1 | -- |

| Model | Amps* | Foot- Print (Ft2) | Ship Weight (Lbs.) |
| --- | --- | --- | --- |
| 300A | 3 | 4.3 | 410 |
| 400A | 4 | 4.7 | 465 |
| 500A | 4 | 5.7 | 505 |
| 700A | 5 | 7.3 | 550 |
| 850A | 5 | 8.3 | 580 |

*Current draw is for heater only.
(Supply breaker must have delayed trip.)

|  | CLEARANCES (in.) |
| --- | --- |
|  | Certified Minimum | Service Minimum |
| Front | 24 | 24 |
| Rear | 24 | 24 |
| Right | 0 | 0 |
| Left | 0 | 0 |
| Top | 12 | 24 |
| Floor | 0 | -- |
| Vent | 1 | -- |

* Current draw is for heater only.

(Supply breaker must have delayed trip.)

* Current draw is for heater only.

(Supply breaker must have delayed trip.)

|  | CLEARANCES (in.) |
| --- | --- |
|  | Certified Minimum | Service Minimum |
| Front | 24 | 24 |
| Rear | 24 | 24 |
| Right | 0 | 0 |
| Left | 0 | 0 |
| Top | 12 | 24 |
| Floor | 0 | -- |
| Vent | 1 | -- |

|  | CLEARANCES (in.) |
| --- | --- |
|  | Certified Minimum | Service Minimum |
| Front | 24 | 24 |
| Rear | 24 | 24 |
| Right | 0 | 0 |
| Left | 0 | 0 |
| Top | 12 | 24 |
| Floor | 0 | -- |
| Vent | 1 | -- |

|  | CLEARANCES (in.) |
| --- | --- |
|  | Certified Minimum | Service Minimum |
| Front | 24 | 24 |
| Rear | 24 | 24 |
| Right | 0 | 0 |
| Left | 0 | 0 |
| Top | 12 | 24 |
| Floor | 0 | -- |
| Vent | 1 | -- |

Raypak, Inc. • Eastman Avenue, Oxnard, CA 93030 • (805) 278-5300 • (805) 872-9725 • www.raypak.com