# Delta Limited® - Type WH

## Water Heaters
Models 989B-2339B

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

100% Factory Fire Tested

Efficiency: Up to 85%

Maximum Setpoint: 150°F

Maximum Outlet Temperature: 200°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Year Thermal Shock Warranty

Limited Ten-Year Cupro-Nickel Heat Exchanger Warranty

Shown with outdoor 
air inlet and pump covers

Limited Five-Year Copper Heat Exchanger Warranty

PolyTuf Powder Coated Cabinet

Combustible Floor Shield Required

Proudly Assembled in the U.S.A.

Fan-Assisted

Patented Burner Security Blanket

#### Heat Exchanger

HLW Stamp

Headers

Glass-Lined Cast Iron – Standard

A-1 Bronze

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

- Copper (Std.) 85%

- Cupro-Nickel 83.1%

ASME Steel Tube Sheet

Silicone High Temp O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

A-6 Right

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

100% Shut-Off/Lockout

Hot Surface Ignition

Ignition Module

- 3-Try Standard

- C-6 Single-Try

Remote Flame Sensor

High Limit Control, Manual Reset

On/Off Power Switch

Manual Shut-Off, Front-Mounted Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Pump Time Delay Relay

Status Display Lights

#### Gas Train

Manual Gas Shut-Off Valve(s)

Combination Valves

Low Gas Pressure Switch, Manual

Firing Mode

2-Stage: Model 989B

3-Stage: Model 1259B

4-Stage: Models 1529B-2339B

Fuel

Natural Gas

Propane Gas

Design Certified - 
ANSI Z21.10.3/CSA 4.3

#### Burner

Ultra-Low NOx: Less than 20 PPM

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

AB-1953 Verified

CSA Low Lead Certified ≤ .25% Lead

#### Venting

Category I/III Cupro-Nickel

Category II/IV Copper

Vent Location

Top, Outdoor – Standard

D-20 Top, Indoor

D-14 Rear

Vent Termination Cap

D-11 Outdoor

D-15 Indoor, Horizontal

Indoor, Vertical (by others)

Extractor – Optional

By others

Not required

Delta Limited models not approved for use in California

Temperature Controls

B-2	Tankstat, Single-Stage 
(100-200°F)

B-3	Tankstat, 2-Stage (100-200°F)

B-26	TempTracker Digital Controller, 2-Stage

B-21	TempTracker Digital Controller, 4-Stage

B-  	TempTracker Mod+ (Loose) Up to 16 Boilers

#### Options

C-6	Ignition Module, Manual Reset

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 
1, 60Hz
Water Hardness:       GPG

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Run (See 1000.19)

S-2	High Gas Pressure Switch, Manual

X-1	SureRack® Kit

X-2	SureRack Add-on

For Metric information, see Catalog

#### Regulatory Agency Requirements

For Metric information, see Catalog

For Metric information, see Catalog

#### Delta Limited – Type WH

#### Models 989B-2339B	Model

NOTE
Pump location varies based on model selected

Raypak, Inc.  2151 Eastman Avenue, Oxnard, CA  93030  (805) 278-5300  Fax (800) 872-9725  www.raypak.com

|  | SPECIFICATIONS |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | MBTUH |  |  | Firing Stages | A Width | K | T | W | Amp. Draw* | Approx. Shipping Wt. (Lbs.) |
|  | Input | Output 85% | Output 83.1% |  |  |  |  |  |  |  |
| 989B | 990 | 842 | 823 | 3 | 57-1/8 | 10 | 10 | 16-13/16 | <12 | 900 |
| 1259B | 1260 | 1071 | 1047 | 4 | 68-1/2 | 12 |  | 20-9/16 |  | 1010 |
| 1529B | 1530 | 1301 | 1271 | 4 | 79-7/8 | 12 |  | 24-3/8 |  | 1225 |
| 1799B | 1800 | 1530 | 1496 | 4 | 91-1/8 | 14 |  | 28-1/8 |  | 1350 |
| 1999B | 2070 | 1699 | 1661 | 4 | 102-1/2 | 14 |  | 31-15/16 |  | 1450 |
| 2069B | 2070 | 1760 | 1720 | 4 | 102-1/2 | 14 |  | 31-15/16 |  | 1450 |
| 2339B | 2340 | 1989 | 1945 | 4 | 113-7/8 | 16 |  | 35-11/16 |  | 1520 |

- Rates shown are for natural or propane gas and elevations up to 4,500 feet. For installations above 4,500 feet, please contact manufacturer.

- Recommended natural gas supply pressure is 7.0 – 10.5 in. WC. Recommended propane gas supply pressure is 11.0 – 13.0 in. WC.

- Amp draw is heater only less pump

#### Delta Limited – Type WH

#### Models 989B-2339B	Model

| Model | 83.1% System Flow and Head Loss |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25** Grains Per Gallon |  |  |  |  |
|  | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) |
| 989B | 28 | 60 | 2.7 | 2 1/2 | 5.2 | 17 | 98 | 7.3 | 2 1/2 | 13.3 | 13 | 132 | 13.1 | 2 1/2 | 23.6 |
| 1259B | 28 | 75 | 4.8 | 2 1/2 | 8.5 | 18 | 115 | 11.3 | 2 1/2 | 19.4 | 16 | 132 | 14.8 | 2 1/2 | 25.3 |
| 1529B | 30 | 86 | 7.1 | 2 1/2 | 11.9 | 21 | 120 | 13.7 | 2 1/2 | 22.5 | 19 | 132 | 16.5 | 2 1/2 | 27.0 |
| 1799B | 30 | 102 | 10.9 | 2 1/2 | 17.4 | 25 | 120 | 15.1 | 2 1/2 | 23.9 | 23 | 132 | 18.3 | 2 1/2 | 28.7 |
| 1999B | 30 | 112 | 13.9 | 2 1/2 | 21.6 | 25 | 132 | 19.0 | 2 1/2 | 29.5 | 25 | 132 | 19.0 | 2 1/2 | 29.5 |
| 2069B | 30 | 117 | 15.1 | 2 1/2 | 23.4 | 26 | 132 | 19.0 | 2 1/2 | 29.5 | 26 | 132 | 19.0 | 2 1/2 | 29.5 |
| 2339B | 30 | 132 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 |

| Model | 85% System Flow and Head Loss |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25** Grains Per Gallon |  |  |  |  |
|  | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) |
| 989B | 28 | 60 | 2.7 | 2 1/2 | 5.2 | 17 | 98 | 7.3 | 2 1/2 | 13.3 | 13 | 132 | 13.1 | 2 1/2 | 23.6 |
| 1259B | 28 | 76 | 4.8 | 2 1/2 | 8.5 | 19 | 115 | 11.3 | 2 1/2 | 19.4 | 16 | 132 | 14.8 | 2 1/2 | 25.3 |
| 1529B | 32 | 83 | 7.1 | 2 1/2 | 11.9 | 22 | 120 | 13.7 | 2 1/2 | 22.5 | 20 | 132 | 16.5 | 2 1/2 | 27.0 |
| 1799B | 32 | 98 | 10.9 | 2 1/2 | 17.4 | 26 | 120 | 15.1 | 2 1/2 | 23.9 | 23 | 132 | 18.3 | 2 1/2 | 28.7 |
| 1999B | 32 | 108 | 13.9 | 2 1/2 | 21.6 | 26 | 132 | 19.0 | 2 1/2 | 29.5 | 26 | 132 | 19.0 | 2 1/2 | 29.5 |
| 2069B | 32 | 112 | 15.1 | 2 1/2 | 23.4 | 27 | 132 | 19.0 | 2 1/2 | 29.5 | 27 | 132 | 19.0 | 2 1/2 | 29.5 |
| 2339B | 32 | 126 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 |

| Model | 83.1% RECOVERY RATES (GPH) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Temperature Rise (°F) |  |  |  |  |  |  |  |  |
|  | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 100° |
| 989B | 4986 | 3324 | 2493 | 1994 | 1662 | 1425 | 1247 | 1108 | 997 |
| 1259B | 6346 | 4231 | 3173 | 2538 | 2115 | 1813 | 1586 | 1410 | 1269 |
| 1529B | 7706 | 5137 | 3853 | 3082 | 2569 | 2202 | 1926 | 1712 | 1541 |
| 1799B | 9065 | 6044 | 4533 | 3626 | 3022 | 2590 | 2266 | 2015 | 1813 |
| 1999B | 10068 | 6712 | 5034 | 4027 | 3356 | 2876 | 2517 | 2237 | 2014 |
| 2069B | 10425 | 6950 | 5213 | 4170 | 3475 | 2979 | 2606 | 2317 | 2085 |
| 2339B | 11785 | 7857 | 5893 | 4714 | 3928 | 3367 | 2946 | 2619 | 2357 |

| Model | 85% RECOVERY RATES (GPH) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Temperature Rise (°F) |  |  |  |  |  |  |  |  |
|  | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 100° |
| 989B | 5100 | 3400 | 2550 | 2040 | 1700 | 1457 | 1275 | 1133 | 1020 |
| 1259B | 6491 | 4327 | 3245 | 2596 | 2164 | 1855 | 1623 | 1442 | 1298 |
| 1529B | 7882 | 5255 | 3941 | 3153 | 2627 | 2252 | 1970 | 1752 | 1576 |
| 1799B | 9273 | 6182 | 4636 | 3709 | 3091 | 2649 | 2318 | 2061 | 1855 |
| 1999B | 10298 | 6865 | 5149 | 4119 | 3433 | 2942 | 2574 | 2288 | 2060 |
| 2069B | 10664 | 7109 | 5332 | 4265 | 3555 | 3047 | 2666 | 2370 | 2133 |
| 2339B | 12055 | 8036 | 6027 | 4822 | 4018 | 3444 | 3014 | 2679 | 2411 |

Raypak, Inc.  2151 Eastman Avenue, Oxnard, CA  93030  (805) 278-5300  Fax (800) 872-9725  www.raypak.com

SHL includes 50 ft of tubing each way (100 total)

** Must use optional cupro-nickel tubes. For hardness exceeding 25 GPG, must use water softener

Basis for minimum flow is 55 GPM or 30°F ∆T, 132 GPM for maximum flow