Job:

# Raytherm® - Type WH

## Water Heaters
Commercial

Models 2100 - 4001

Engineer:

Contractor:

Prepared By:

Model:  	     	Indoor	Date:

Efficient

- 82% thermal efficiency

Thermal shock proof

- Limited 25-year thermal shock warranty

Lightweight

- A floor load of 70 lbs./sq. ft. or less

Dependable

- The simple atmospheric design provides a low cost and long life solution.

Low water operating temperature

Operates with water temperature as low as 105°F
without condensing

Proudly Assembled in the USA

#### Heat exchanger

- ASME HLW Stamped;
 160 PSIG MAWP

- National Board

- Headers

Bronze (standard)

A-2 Glass-lined cast iron (optional)

- Fin tubing

Copper (standard)

A-3 Cupronickel (optional)

- ASME Steel tube sheet

- Silicone O-Rings

- Pressure relief valve

- 125 PSIG ASME (standard)

- A-15 150 PSIG PRV (optional)

- T&P Gauge

- Water connections

Left hand (standard)

A-6 Right hand (optional)

- Two-pass Flow Configuration

#### Controls

- 120V, 60Hz, 1 Ph Power Supply

- 120/24V Transformer

- 100% Pilot shut-off/lockout

- Electronic, Intermittent Ignition (IID) Pilot

- High limit control, manual reset – 200°F

- High limit control, auto reset – 200°F
Models 3001-4001

- On/off switch

- Flow switch

- Economaster II pump time delay

#### Gas control train

- Manual main gas shut-off valve

- Main gas pressure regulator

- Redundant safety shut-off valve

- Control valve

- Firing mode

WH-1 On/off

WH-3 2-stage firing

- Fuel

Natural gas

Propane gas (min. grade HD-5)

- Design Certified ANSI Z21.10.3

#### Construction

- Front controls

- Stainless steel burners

- Baked enamel paint

- Built-in draft diverter

- Draft inducer (optional)

D-2 Motorized draft inducer – 
indoor

- CSA Low Lead Certified ≤ .25% Lead

#### Water heater controllers
Required on Model WH2 only

B-2	Single-stage tankstat 
(100-180°F), loose (WH1)

B-3	2-Stage tankstat (100-180°F), loose (WH3)

B-21	4-Stage digital (WH3)

B-26	2-Stage digital (WH3)

B-40	TempTracker MOD

modulating controller 
mounted (WH3)

Additional safety controls

F-9	Low water cut-off probe

I-3	High limit control, auto reset, 180°F

S-1	Low gas pressure switch, manual

S-2	High gas pressure switch, manual (standard on models 3001-4001)

#### Regulatory agency requirements

Raytherm - Type WH

Models 2100-4100	Model

Models 2100 - 4001

| Model | MBTUH (kW) Natural & Propane Gas |  | Dimensions in. (mm) |  |  |  | Electrical Rating | Approx. Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Width | Gas Conn. | Water Conn. | Flue Dia | Less than 8.0 amps without pump at 120VAC |  |
|  | Input | Output | A | G | H | K |  |  |
| H-2100 | 2100 (615) | 1722 (505) | 61 (1549) | (a) | 3 (b) | 24 |  | 1400 |
| H-2500 | 2499 (732) | 2049.2 (601) | 70 (1778) | (a) | 3 (b) | 26 |  | 1580 |
| H-3001 | 3000 (879) | 2460 (721) | 81-1/4 (2064) | 2 | 3 (b) | 28 |  | 1750 |
| H-3500 | 3500 (1026) | 2870 (841) | 92-1/2 (2350) | 2 | 3 (b) | 30 |  | 1920 |
| H-4001 | 4000 (1172) | 3280 (961) | 103-3/4 (2635) | 2 | 3 (b) | 32 |  | 2100 |
| NOTE: Ratings are for elevations up to 2,000 feet. For elevations over 2,000 feet, reduce ratings 4% for every 1,000 feet above sea level |  |  |  |  | (a) 1-1/2” or 2” contingent on boiler type code requirements (b) 4” on one-pass option |  |  |  |

HEATER RATES OF FLOW AND PRESSURE DROPS

| Model No. | 20°F T |  | 30°F T |  | 40°F T |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | GPM | P (ft) | GPM | P (ft) | GPM | P (ft) |
| WH-2100 | 172 | 11.0 | 115 | 4.9 | N/A | N/A |
| WH-2500 | N/A | N/A | 137 | 7.5 | 102 | 4.3 |
| WH-3001 | N/A | N/A | 164 | 11.2 | 123 | 6.5 |
| WH-3500 | N/A | N/A | 191 | 16.8 | 144 | 9.3 |
| WH-4001 | N/A | N/A | N/A | N/A | 164 | 12.8 |

HEATER RECOVERY RATES (GPH)

| Model No. | Temperature Rise |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20°F | 30°F | 40°F | 50°F | 60°F | 80°F | 100°F |
| WH-2100 | 10336 | 6890 | 5168 | 4134 | 3445 | 2584 | 2067 |
| WH-2500 | 12300 | 8200 | 6150 | 4920 | 4100 | 3075 | 2460 |
| WH-3001 | 14765 | 9844 | 7383 | 5906 | 4922 | 3691 | 2953 |
| WH-3500 | 17227 | 11484 | 8613 | 6891 | 5742 | 4301 | 3445 |
| WH-4001 | 19688 | 13125 | 9844 | 7875 | 6563 | 4922 | 3938 |

Note: Maximum acceptable flow through heat exchanger tubes is 200 GPM.

For water hardness between 16 & 25 GPG, a Cupro Nickel heat exchanger is required. For water hardnesses above 25 GPG, a softener/treatment system must be used.

MODELS WH 2100 – 4001

| Model No. | MBTUH |  | Width | Overall Height | Gas Conn. | Water Conn. | Flue Dia. | Approx. Shipping Weight (lbs) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output | A | B | G | H | K |  |
| WH-2100 | 2100 | 1722 | 61 | 68-1/4 | * | 3 | 24 | 1400 |
| WH-2500 | 2499 | 2049 | 70 | 68-1/4 | * | 3 | 26 | 1580 |
| WH-3001 | 3000 | 2460 | 81-1/4 | 68-1/4 | 2 | 3 | 28 | 1750 |
| WH-3500 | 3500 | 2870 | 92-1/2 | 68-1/4 | 2 | 3 | 30 | 1920 |
| WH-4001 | 4000 | 3280 | 103-3/4 | 68-1/4 | 2 | 3 | 32 | 2100 |

*	1-1/2” or 2”, contingent on water heater type code requirements

NOTES:	Dimensions are in inches.
Ratings are for elevations up to 2,000 feet. For elevations over 2,000 feet, reduce ratings 4% for every 1,000 feet above sea level.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (805) 278-5468    www.raypak.com

| Models | Electrical Rating |  |
| --- | --- | --- |
|  | W/Pump | W/O Pump |
| 2100-4001 | 951276 pump* 11 Amps @ 230VAC | < 8 Amp @ 120VAC |
|  | 22 Amps @ 110VAC |  |

* Pump requires separate power supply