Job: 	     ______________

# TempTracker Mod+ Hybrid™
Modulating Controllers

# For Controlling Raypak Condensing and/or Non-Condensing Boilers and Water Heaters

Engineer: 	     ______________

Contractor: 	     ______________

Prepared By: 	     ______________

Date: 	     ______________

TempTracker Mod+ Hybrid is designed to sequence multiple condensing and/or non-condensing boilers up to 16 total units in a single system, and is capable of controlling Raypak modulating or stage-fired boilers. It is available loose with Hi Delta, Raytherm, MVB, XTherm and XFyre boilers and water heaters. This control can be used for space heating and hot water supply, including outdoor reset for heating systems. It monitors and displays system temperatures on all applications as well as monitors outdoor temperature when an outdoor sensor is utilized.

Proudly Made in the USA

#### Features

- 1-4 boilers/stages

- Lead/Lag Rotation

- PID logic

- 5 LED Status Lights

- LCD digital display

- System Pump Relay – Pilot Duty

- Remote Thermostat Connection

- NEMA 1 enclosure

- System water sensor

- Outdoor air sensor

- Reset Ratio 1:4 to 4:1

- 120 VAC, 60 Hz, 12 VA Supply Power

- Relay Ratings
1A Inductive, 6A Resistive at 120 VAC, 60 Hz
15A total for all circuits

Programmable Functions

- Adjustable outdoor reset

- 4-20 mA or 0-10 VDC output

- System water temperature

  - Heating – 50º - 220 F

  - Temp to Indirect DHW – 140º - 200 F

- Switch differential (5º to 20 F)

- Outdoor cutoff (20 to 100 F)

- Indirect Domestic Hot Water with/without Priority

- System pump-off delay (0 to 360 min.)

- Temperature measurement (F or C)

- BACnet compatible (requires B-62)

Model Information

B-36	Up to 4 Units

B-37	Up to 10 Units

B-38	Up to 16 Units

Options

B-39	4-20mA Remote Set Point

B-62	BACnet MS/TP

#### Specifications

Voltage Input:	.	.	.	.	.	.	120 VAC 60 Hz

Power Consumption:	.	.	.	.	.	12 VA Max

Operating Temperature:	.	.	.	.	20°F/-6°C to 130°F/54°C

Operating Humidity:	.	.	.	.	.	20% to 80% non-condensing

Dimensions:	.	.	.	.	.	.	11"W x 9" H x 3 ¾" D

Weight:	.	.	.	.	.	.	.	2.5 pounds

#### TempTracker MOD+ Hybrid Specifications

Pump Output:	.	.	.	.	.	.	1 N.O. S.P.S.T

Modulating Boiler Modes:	.	.	.	.	Auto, Manual, Standby, On, Off

Staging Boiler Modes:	.	.	.	.	.	Auto, Standby, On, Off

Modulating Output Types:	.	.	.	.	4-20mA and 0-10V

Sequencing Output Types:	.	.	.	.	On/Off, 2-Stage, 3-Stage, or 4-Stage

Output Relay Ratings:	.	.	.	.	.	1 Amp inductive (⅛ HP), 6 Amp resistive at 120 VAC

Add-On Extension Panels:	.	.	.	.	up two Extension Panels using RS485 (RJ45 or RJ11)

Modulation Modes:	.	.	.	.	.	Normal or Parallel

Sequencing Modes:	.	.	.	.	.	Lo/Hi/Lo/Hi or Lo/lo/Hi/Hi

Temperature Display:	.	.	.	.	.	Fahrenheit or Celsius

Display:	.	.	.	.	.	.	Graphical Alphanumeric (up to 7 rows x 21 char. each)

LED:	.	.	.	.	.	.	.	1 System Output relay, 4 Boiler Output relays

Outdoor Cutoff Range:	.	.	.	.	.	20°F/-6°C to 100°F, ON and OFF

Reset Ratio Range:	.	.	.	.	.	(1:4) to (4:1) (Outdoor : System Water)

Minimum Water Temperature:	.	.	.	.	50°F/10°C to 170°F/77°C

Maximum Water Temperature:	.	.	.	.	90°F/32°C to 240°F/116°C

Indirect Domestic Hot Water:	.	.	.	.	with Priority or without Priority

Schedules:	.	.	.	.	.	.	1 Day and 1 Night (Setback) setting per day

Night Setback:	.	.	.	.	.	.	0°F°/0°C° to 75°F°/42°C°

Power Backup:	.	.	.	.	.	.	Lithium coin battery, 100 days minimum 5 year

External Inputs:	.	.	.	.	.	Shutdown, Tstat, and Setback Input, and Prove and

#### Extension Specifications

(Each Extension can add up to (6) additional boiler stages. A maximum of two Extensions can be used.)

Boiler Outputs:	.	.	.	.	.	.	(6) N.O. S.P.S.T.

Modulating Output Types:	.	.	.	.	(6) 4-20mA and 0-10V

Output Relay Ratings:	.	.	.	.	.	1 Amp inductive (⅛ HP), 6Amp resistive at 120 VAC 6

Connection to TempTracker mod+ Hybrid and another extension:

Two RS485 connections using 6 wire RJ11 cable (Cable is provided)

DHW Call Input. (Dry Contacts Only)

replacement (Maintains Clock in power outages)

DHW Call Input. (Dry Contacts Only)

60 Hz, 15 A total for all circuits

9”

11” TYP