Job:

# Power Vent

# For Raytherm®
Models 514-1826

Engineer:

Contractor:

Prepared By: 	     		Date:

Versatile

Suitable for use with hydronic heating boilers and hot water heaters

Permits sidewall venting

Allows use of smaller diameter vent pipe

Efficient

Maintains thermal efficiency of 82% on all appliance sizes

Multi-Position Capability

Fan discharge adjusts to match position of 
vent pipe, reducing number of fittings

Draft Control

Barometric damper provides overfire draft
when necessary

# Features

- Induced draft

- Barometric damper

- Plenum sized for appliance capacity

- Pre-wired and mounted, or shipped loose for field installation

- Air flow proving switch, mounted and wired

- Fan motor relay, mounted and wired

- Heavy-duty galvanized steel cabinet

- Polytuf powder coat finish

- Indoor construction

- Easy installation

- Limited one-year warranty

# Options

Shipped loose for field mounting

Shipped mounted on unit

#### Power Vent

#### For Raytherm 514 - 1826	Model

FIVE DIFFERENT DISCHARGE POSITIONS

| Raytherm Model | MBTU | Max. Run (ft.) |  | Dimensions (in.) |  |  |  |  |  | Electrical Ratings at 120V |  |  | Max. CFM @ 70ºF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Vert. | Horiz. | A | B | C | D | E | F | W/out Pump | W/ Pump | HP |  |
| 514 | 512 | 20 | 40 | 17-7/8 | 15-7/8 | 20 | 8 | 20-1/4 | 9-3/4 | < 10 Amps | < 16 Amps | 1/3 | 925 |
| 624 | 627 | 20 | 22 | 17-7/8 | 15-7/8 | 20 | 8 | 20-1/4 | 9-3/4 | < 10 Amps | < 16 Amps | 1/3 | 925 |
| 724 | 726 | 20 | 13 | 17-7/8 | 15-7/8 | 20 | 8 | 20-1/4 | 9-3/4 | < 10 Amps | < 16 Amps | 1/3 | 925 |
| 824 | 825 | 20 | 22 | 17-7/8 | 15-7/8 | 20 | 8 | 20-1/4 | 9-3/4 | < 10 Amps | < 16 Amps | 1/3 | 925 |
| 962 | 962 | 20 | 12 | 17-7/8 | 15-7/8 | 20 | 8 | 21-13/16 | 11-5/16 | < 10 Amps | < 16 Amps | 1/3 | 925 |
| 1125 | 1125 | 20 | 5* | 17-7/8 | 15-7/8 | 20 | 8* | 21-13/16 | 11-5/16 | < 10 Amps | < 16 Amps | 1/3 | 925 |
| 1223 | 1223 | 20 | 4** | 17-7/8 | 15-7/8 | 20 | 8** | 21-13/16 | 11-5/16 | < 10 Amps | < 16 Amps | 1/3 | 925 |
| 1336 | 1336 | 20 | 21 | 21 | 18-5/8 | 42 | 10 | 23-1/2 | 12-1/2 | < 18 Amps | < 24 Amps | 1 | 1425 |
| 1468 | 1468 | 20 | 15 | 21 | 18-5/8 | 42 | 10 | 23-1/2 | 12-1/2 | < 18 Amps | < 24 Amps | 1 | 1425 |
| 1631 | 1631 | 20 | 10 | 21 | 18-5/8 | 42 | 10 | 23-1/2 | 12-1/2 | < 18 Amps | < 24 Amps | 1 | 1425 |
| 1826 | 1826 | 20 | 5* | 21 | 18-5/8 | 42 | 10* | 23-1/2 | 12-1/2 | <18 Amps | < 24 Amps | 1 | 1425 |

*	Maximum horizontal run can be increased to 70 ft. by using one size larger vent pipe. The larger pipe must be used starting at the power vent outlet. (Transition piece not supplied by Raypak.)

**	Maximum horizontal run can be increased to 32 ft. by using two sizes larger vent pipe. The larger pipe must be used starting at the power vent outlet. (Transition piece not supplied by Raypak.)

NOTES:	1.	Vent pipe sizes are based on: standard vertical discharge, using one 90° elbow and one tee with a 90° turn; 300°F nominal flue temperature; and sea-level operation. For installation under other conditions, please consult the factory.

2.	Flue pipe must meet Category III appliance venting requirements.

3.	Follow installation instructions provided by power vent manufacturer.

4.	Vent terminal should be installed with the motor on the right or front side of the boiler.

5.	Overhang dimensions extend over front of appliance, but do not exceed service clearances.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com