Job:

# Raytherm® - Type WH

## Water Heaters
Commercial

Models 181-401

Engineer:

Contractor:

Low NOx

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

LOW NOx

- Less than 40 nanograms per joule

EFFICIENT

- 82% thermal efficiency – highest of any atmospheric
water heater available today

THERMAL-SHOCK PROOF

- Twenty-year warranty against thermal shock damage
up to 150°F differential

- Maximum operating temperature: 200°F

LIGHTWEIGHT

- A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

- Cuts fuel costs substantially because the standby and
radiation losses associated with other tank-type water 
heaters are eliminated

LOW WATER OPERATING TEMPERATURE

Proudly Assembled in the USA

Operates with water temperature as low as
105°F without condensing

Indoor Model Illustrated

#### Heat Exchanger

- ASME Inspected and Stamped
160 PSIG

- National Board Approved

- Headers

Bronze – Standard

Glass-lined Cast Iron – Option A-2

- Finned Tubing

Copper – Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone O-Rings

- ASME Pressure Relief Valve

- 125 PSIG – Standard

- 150 PSIG – Option A-16

- Temperature and Pressure Gauge,
Shipped Loose

- Water Connections

Left Hand – Standard

Right Hand – Option A-6

- Two-pass Flow Configuration

- Pump – Optional

Mounted, 1/8 HP, 120 VAC, 1, 60 Hz

#### Controls

- 120V, 60Hz, 1 Ph Power Supply

- 120/24V Transformer

- 100% Pilot Shut-off/Lockout

- Electronic, Intermittent Ignition (IID) Pilot

#### Controls (cont'd)

- High Limit Control, Manual Reset – 200°F

- On/Off Switch

- Flow Switch

- Economaster II Pump Time Delay

#### Gas Control Train

- Natural Gas

- Manual Main Gas Shut-off Cock

- Main Gas Pressure Regulator

- Redundant Safety Shut-off Valve

- Control Valve

- Firing Mode

On/Off (WH1)

2-stage Firing (WH3)

- Design Certified ANSI Z21.10.3/
CSA 4.3

#### Construction

- Front Controls

- Stainless Steel, Fan-assisted Burners

- PolyTuf Powder Coat Finish

- Vent Selection

Indoor Drafthood – Option D-10

Outdoor Stackless Top – 
Option D-11

- Base – Optional

Combustible Floor Shield – 
Option J-1

- CSA Low Lead Certified ≤ .25 Lead

#### Temperature Controls

B-2	Single-Stage Tankstat 
(100-180°F)

B-3	2-Stage Tankstat (100-180°F)

B-26	2-Stage Digital

B-21	4-Stage Digital

#### Additional Safety Controls

I-3	High Limit Control, Auto Reset, 180°F

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

Raytherm - Type WH

Low NOx

Models 181-401	Model

*

|  |  |  | Dimensions (Inches) |  |  |  | Shipping Weight (Lbs.) – Approx. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model No. | MBTUH Input | MBTUH Output | Width A | Height C | J | Flue Dia. K |  |  |
|  |  |  |  |  |  |  | No Pump | w/ Pump |
| WH-181* | 181 | 148 | 18-1/4 | 62-5/8 | 12-1/16 | 6 | 191 | 221 |
| WH-261 | 264 | 216 | 22-3/8 | 62-7/8 | 11-1/8 | 7 | 214 | 244 |
| WH-331 | 334 | 274 | 25-3/4 | 63-3/4 | 10-3/4 | 8 | 234 | 264 |
| WH-401* | 399 | 327 | 29-1/4 | 65-3/8 | 12-1/2 | 9 | 253 | 283 |

*	Exceptions on WH3 (2-stage-fired) models:

- Model WH3-181 has an 18-1/4” gas connection

- Model WH3-401 has 375 MBTUH Input and 308 MBTUH Output

HEATER RATES OF FLOW AND PRESSURE DROPS

| Model No. | 10° ∆T |  | 20° ∆T |  | 30° ∆T |  | 40°∆T |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) |
| WH-181 | 30 | 4.2 | N/A | N/A | N/A | N/A | N/A | N/A |
| WH-261 | 43 | 8.5 | 22 | 2.2 | N/A | N/A | N/A | N/A |
| WH-331 | N/A | N/A | 27 | 3.4 | N/A | N/A | N/A | N/A |
| WH-401 | N/A | N/A | 33 | 5.2 | 22 | 2.3 | N/A | N/A |

N/A – Not Applicable

HEATER RECOVERY RATES

| Model No. | Temperature Rise |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 10°F | 20°F | 30°F | 40°F | 50°F | 60°F | 80°F | 100°F |
|  | Gallons Per Hour |  |  |  |  |  |  |  |
| WH-181 | 1794 | 897 | 598 | 448 | 359 | 299 | 224 | 179 |
| WH-261 | 2618 | 1309 | 873 | 655 | 524 | 436 | 327 | 262 |
| WH-331 | 3321 | 1661 | 1107 | 830 | 664 | 554 | 415 | 332 |
| WH-401 | 3964 | 1982 | 1321 | 991 | 793 | 661 | 495 | 396 |

NOTE:	Ratings shown are for elevations up to 5,000 feet for indoor or outdoor installations. For elevations over 5,000 feet, contact manufacturer.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com