# Hi Delta FlexGas® - Type WH

## Dual-Fuel Water Heaters
Models 992CD-2342CD

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

- 100% Factory Fire Tested

- Thermal Efficiency: Up to 85%

- Versa IC® Controller with LCD Display

- Maximum Setpoint: 150°F

- Maximum Outlet Temperature: 200°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal-Shock Proof Heat Exchanger

- Limited Twenty-Year Thermal Shock Warranty

- Limited Ten-Year Cupro-Nickel Heat Exchanger Warranty

- Limited Five-Year Copper Heat Exchanger Warranty

- Full Safety Diagnostics with Fault History

Patent Nos. 6,904,873 & 7,044,124; other patents pending

PolyTuf Powder Coated Cabinet

- No Combustible Floor Shield Required

- Fan-Assisted

Proudly Assembled in the USA

Patented Burner Security Blanket

- Ultra-Low NOx – SCAQMD 1146.2 Certified (992C – 1802C)

- Cascade up to 4 Heaters – No External Sequencer Required

#### Heat Exchanger

Headers

Brass – Standard

A-2 Glass-Lined Cast Iron

ASME Inspected and HLW Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

- Copper (Std.) 85%

- Cupro-Nickel 83.1%

ASME Steel Tube Sheet

Silicone High-Temp. O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

#### A-6 Right Hand

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

Versa IC® Integrated Control

100% Shut-Off/Lockout

Hot Surface Ignition

Ignition Module

- 3-Try – Standard

- C-6 Single Try

Remote Flame Sensor

Fixed High Limit, Manual Reset 240°F

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Programmable Pump Time Delays

Heater

Recirculation

Enable/Disable

#### Controls – cont.

LCD Display; Status, Fault and Diagnostics

Cold Water Protection Function

- Optional CWR Variable-Speed Pump

- (See Cat. 5000.73)

Modbus RTU BMS Port (Up to 115K Baud,   See Cat. 5000.73)

- B-85 – BMS Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

- B-86 – BMS Gateway - LonWorks

#### Gas Train

Manual Gas Shut-Off Valve(s)

Combo Valve(s)

Firing Mode

3-Stage (WH8): Model 992C

4-Stage (WH9): Models 1262C – 2342C

Natural/Propane Gas

Design Certified - ANSI Z21.10.3/CSA 4.3

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

Powder Coat Finish

CSA Low Lead Certified (≤ .25% Lead)

#### Venting

Vent Category I/III Cupro-Nickel

Vent Category II/IV Copper

Vent Location

Top – Standard

D-14 Rear

Vent Termination Cap

D-11 Outdoor

D-15 Indoor, Horizontal

Indoor, Vertical (by others)

Combustion Air

D-17 In-Line Filter Kit (TruSeal only)

D-16 Air Intake Elbow

#### Venting – cont.

Extractor – Optional

By others

Not required

#### Burner

Ultra-Low NOx: Less than 20 PPM

Options

D-21	TruSeal Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1, 60Hz

Bronze
 Mounted	 Loose

Front	 Rear

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack® Kit

X-2	SureRack Add-on

Additional Options or Accessories

#### Multi-Boiler Temperature Controllers

TempTracker Mod+ Hybrid

B-36, 2-4 Heaters

B-37, 5-10 Heaters

B-38, 11-16 Heaters

B-39 EMS 4-20mA Remote Setpoint Interface Module

B-62 BACnet MS/TP Interface

#### Hi Delta FlexGas – Type WH
Models 992CD-2342CD	Model _     _____

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

NOTE:  Pump location varies based on model and application.

|  | SPECIFICATIONS |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | MBTUH |  |  | Firing Stages | A Width | K | T | W | Amp. Draw* | Approx. Shipping Wt. (Lbs.) |
|  | Input | Output 85% | Output 83.1% |  |  |  |  |  |  |  |
| 992CD | 990 | 842 | 823 | 3 | 57-1/8 | 10 | 10 | 16-13/16 | <12 | 900 |
| 1262CD | 1260 | 1071 | 1047 | 4 | 68-1/2 | 12 |  | 20-9/16 |  | 1010 |
| 1532CD | 1530 | 1301 | 1271 | 4 | 79-7/8 | 12 |  | 24-3/8 |  | 1225 |
| 1802CD | 1800 | 1530 | 1496 | 4 | 91-1/8 | 14 |  | 28-1/8 |  | 1350 |
| 2072CD | 2070 | 1760 | 1720 | 4 | 102-1/2 | 14 |  | 31-15/16 |  | 1450 |
| 2342CD | 2340 | 1989 | 1945 | 4 | 113-7/8 | 16 |  | 35-11/16 |  | 1520 |

*Without pump.

NOTES:	1. Dimensions are in inches.

2.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

3. Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.

#### Hi Delta FlexGas – Type WH
Models 992CD-2342CD                                                  Model

| Model | 83.1% System Flow and Head Loss |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25** Grains Per Gallon |  |  |  |  |
|  | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) |
| 992CD | 28 | 60 | 2.7 | 2 1/2 | 5.2 | 17 | 98 | 7.3 | 2 1/2 | 13.3 | 13 | 132 | 13.1 | 2 1/2 | 23.6 |
| 1262CD | 28 | 75 | 4.8 | 2 1/2 | 8.5 | 18 | 115 | 11.3 | 2 1/2 | 19.4 | 16 | 132 | 14.8 | 2 1/2 | 25.3 |
| 1532CD | 30 | 86 | 7.1 | 2 1/2 | 11.9 | 21 | 120 | 13.7 | 2 1/2 | 22.5 | 19 | 132 | 16.5 | 2 1/2 | 27.0 |
| 1802CD | 30 | 102 | 10.9 | 2 1/2 | 17.4 | 25 | 120 | 15.1 | 2 1/2 | 23.9 | 23 | 132 | 18.3 | 2 1/2 | 28.7 |
| 2072CD | 30 | 117 | 15.1 | 2 1/2 | 23.4 | 26 | 132 | 19.0 | 2 1/2 | 29.5 | 26 | 132 | 19.0 | 2 1/2 | 29.5 |
| 2342CD | 30 | 132 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 |

| Model | 85% System Flow and Head Loss |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25** Grains Per Gallon |  |  |  |  |
|  | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) |
| 992CD | 28 | 60 | 2.7 | 2 1/2 | 5.2 | 17 | 98 | 7.3 | 2 1/2 | 13.3 | 13 | 132 | 13.1 | 2 1/2 | 23.6 |
| 1262CD | 28 | 76 | 4.8 | 2 1/2 | 8.5 | 19 | 115 | 11.3 | 2 1/2 | 19.4 | 16 | 132 | 14.8 | 2 1/2 | 25.3 |
| 1532CD | 32 | 83 | 7.1 | 2 1/2 | 11.9 | 22 | 120 | 13.7 | 2 1/2 | 22.5 | 20 | 132 | 16.5 | 2 1/2 | 27.0 |
| 1802CD | 32 | 98 | 10.9 | 2 1/2 | 17.4 | 26 | 120 | 15.1 | 2 1/2 | 23.9 | 23 | 132 | 18.3 | 2 1/2 | 28.7 |
| 2072CD | 32 | 112 | 15.1 | 2 1/2 | 23.4 | 27 | 132 | 19.0 | 2 1/2 | 29.5 | 27 | 132 | 19.0 | 2 1/2 | 29.5 |
| 2342CD | 32 | 126 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 |

SHL includes 50 equivalent ft of tubing each way (100 total)

** Must use optional cupro-nickel tubes. For hardness exceeding 25 GPG, must use water softener

Basis for minimum flow  is 55 GPM or 30°F ∆T, 132 GPM for maximum flow

| Model | 83.1% RECOVERY RATES (GPH) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Temperature Rise (°F) |  |  |  |  |  |  |  |  |
|  | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 100° |
| 992CD | 4986 | 3324 | 2493 | 1994 | 1662 | 1425 | 1247 | 1108 | 997 |
| 1262CD | 6346 | 4231 | 3173 | 2538 | 2115 | 1813 | 1586 | 1410 | 1269 |
| 1532CD | 7706 | 5137 | 3853 | 3082 | 2569 | 2202 | 1926 | 1712 | 1541 |
| 1802CD | 9065 | 6044 | 4533 | 3626 | 3022 | 2590 | 2266 | 2015 | 1813 |
| 2072CD | 10425 | 6950 | 5213 | 4170 | 3475 | 2979 | 2606 | 2317 | 2085 |
| 2342CD | 11785 | 7857 | 5893 | 4714 | 3928 | 3367 | 2946 | 2619 | 2357 |

| Model | 85% RECOVERY RATES (GPH) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Temperature Rise (°F) |  |  |  |  |  |  |  |  |
|  | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 100° |
| 992CD | 5100 | 3400 | 2550 | 2040 | 1700 | 1457 | 1275 | 1133 | 1020 |
| 1262CD | 6491 | 4327 | 3245 | 2596 | 2164 | 1855 | 1623 | 1442 | 1298 |
| 1532CD | 7882 | 5255 | 3941 | 3153 | 2627 | 2252 | 1970 | 1752 | 1576 |
| 1802CD | 9273 | 6182 | 4636 | 3709 | 3091 | 2649 | 2318 | 2061 | 1855 |
| 2072CD | 10664 | 7109 | 5332 | 4265 | 3555 | 3047 | 2666 | 2370 | 2133 |
| 2342CD | 12055 | 8036 | 6027 | 4822 | 4018 | 3444 | 3014 | 2679 | 2411 |

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com