# Raytherm® - Type WH

## Water Heaters
Commercial

Models 514-824

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

EFFICIENT

82% thermal efficiency – highest of any atmospheric water heater available today

THERMAL SHOCK PROOF

Twenty-year warranty against thermal shock damage
up to 150°F differential

Maximum outlet temperature: 210°F

LIGHTWEIGHT

A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

Cuts fuel costs substantially because the standby and
radiation losses associated with tank-type water heaters are eliminated

LOW WATER OPERATING TEMPERATURE

Proudly Assembled in the USA

Operates with water temperature as low as
105°F without condensing

#### Heat Exchanger

ASME Inspected and Stamped
160 PSIG

National Board Approved

Headers

Bronze – Standard

A-2 Glass-lined Cast Iron

Fin Tubing

Copper – Standard

A-3 Cupro-Nickel

ASME Steel Tube Sheet

Silicone O-Rings

ASME Pressure Relief Valve

- 125 PSIG – Standard

- 150 PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left Hand – Standard

A-6 Right Hand

Two-pass Flow Configuration

Pump – Optional

Mounted, 1/2 HP, 120 VAC, 1 60 Hz

#### Controls

120V, 60Hz, 1 Ph Power Supply

120/24V Transformer

100% Pilot Shut-off/Lockout

Electronic, Intermittent Ignition (IID) Pilot

High Limit Control, Manual Reset –  200°F

On/Off Switch

Flow Switch

Economaster II Pump Time Delay
Gas Control Train

Manual Main Gas Shut-off Cock

Main Gas Pressure Regulator

Redundant Safety Shut-off Valve

Control Valve

Firing Mode

On/Off (WH1)

2-stage Firing (WH3)

Mechanical Modulation (WH2)

(110 - 170°F Outlet)

Fuel

Natural Gas

Propane Gas

#### Construction

Front Controls

Stainless Steel Burners

PolyTuf Powder Coat Finish

Design Certified ANSI Z21.10.3/
CSA 4.3

CSA Low Lead Certified ≤ .25% Lead

Vent Selection

D-10 Drafthood (Indoor)

D-2 Power Vent, Loose

D-11 Stackless Top (Outdoor)

Base – Optional

J-1 Combustible Floor Shield

#### Temperature Controls

B-2	Single-Stage Tankstat 
(100-180°F)

B-3	2-Stage Tankstat (100-180°F)

B-26	2-Stage Digital

B-21	4-Stage Digital

#### Additional Safety Controls

F-9	Low Water Cut-off Probe

I-3	High Limit Control, Auto Reset, 180°F

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

#### Regulatory Agency Requirements

CSD-1 Safety Controls

Raytherm - Type WH

Models 514-824	Model

1 NPT

MODELS WH 514-824

|  | Indoor |  | Outdoor |  | Dimensions (Inches) |  |  | Electrical Rating (Amps) |  | Shipping Weight (Lbs.) – Approx. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model No. | MBTUH Input | MBTUH Output | MBTUH Input | MBTUH Output | Width A | Flue Dia. K | L | W/O Pump | W/ Pump |  |  |
|  |  |  |  |  |  |  |  |  |  | Less Pump | W/ Pump |
| WH - 514 | 511.5 | 419.4 | 511.5 | 419.4 | 32-3/4 | 10 | 25-3/8 | < 4 | < 12 | 475 | 530 |
| WH - 624 | 627.0 | 514.0 | 627.0 | 514.0 | 37-1/2 | 12 | 29-1/2 |  |  | 485 | 540 |
| WH - 724 | 726.0 | 595.0 | 726.0 | 595.0 | 41-5/8 | 12 | 34-1/4 |  |  | 635 | 690 |
| WH - 824 | 825.0 | 676.5 | 825.0 | 676.5 | 45-3/4 | 14 | 38-1/2 |  |  | 645 | 700 |

NOTE:	Ratings shown are for elevations up to 2,000 feet. For elevations over 2,000 feet, reduce ratings at the rate of 4% for each 1,000 feet above sea level.

HEATER RATES OF FLOW AND PRESSURE DROPS

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

| Model No. | 20º ΔT |  | 30º ΔT |  | 40º ΔT |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | GPM | ΔP (ft) | GPM | ΔP (ft) | GPM | ΔP (ft) |
| WH - 514 | 42 | 1.9 | N/A | N/A | N/A | N/A |
| WH - 624 | 51 | 3.0 | N/A | N/A | N/A | N/A |
| WH - 724 | 60 | 4.4 | 40 | 2.0 | N/A | N/A |
| WH – 824 | 68 | 6.0 | 45 | 2.6 | N/A | N/A |

HEATER RECOVERY RATES

N/A – Not Applicable

|  | Temperature Rise |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Model No. | 20ºF | 30ºF | 40ºF | 50ºF | 60ºF | 80ºF | 100ºF |
|  | Gallons Per Hour |  |  |  |  |  |  |
| WH - 514 | 2541 | 1695 | 1271 | 1016 | 847 | 635 | 508 |
| WH - 624 | 3115 | 2077 | 1558 | 1246 | 1038 | 779 | 623 |
| WH - 724 | 3606 | 2404 | 1803 | 1442 | 1202 | 902 | 721 |
| WH - 824 | 4100 | 2733 | 2050 | 1640 | 1367 | 1025 | 820 |