Job:

# Condensing Heat Exchanger (CHX)

## For use with the
Advanced Design Boiler™

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:

Exclusively for use with Raypak’s

ADVANCED DESIGN BOILER™

Boosts ADB efficiency to 98%!

The Raypak Condensing Heat Exchanger utilizes exhaust heat, which is normally wasted, and converts it to useful energy that increases overall operating efficiency.

Applications

- Hydronic Space Heating

- Hot Water Supply

Pool Heating

Advanced Design Boiler with CHX

FEATURES

- Finned cupro nickel tubes

- Patented epoxy coating

- All bronze headers

- AL29-4C Stainless Steel casing

- Polytuf  powder coating on outer shell

- AL29-4C Stainless Steel vent adapter between the CHX and Advanced Design Boiler included

- ASME tested to 150 PSIG working pressure

- Traditional Raypak tube sheet design with high-temperature silicone O-rings

- Condensate drain connection

- Indoor/outdoor construction

- Limited 20 year thermal shock warranty

- Footprint: less than 4.8 ft2

- Ten-year limited warranty

- National Board approved

#### Condensing Heat Exchanger (CHX)	Model

| MODEL | FITS ADB MODEL | A WIDTH | B* HEIGHT | F* | P* | U* | M* | T NPT | K | H NPT | X MIN. | Y | Z | ZZ MIN. | SHIP WT. (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CHX 500 | ADB 500 | 23-1/4 | 24-11/16 | 18-3/4 | 11 | 22-1/4 | 13-3/4 | 1/2 | 6 | 2 | 28 | 8-3/8 | 3-1/2 | 54 | 250 |
| CHX 750 | ADB 750 |  | 30-11/16 | 24-1/8 | 15 | 27-3/4 | 16-1/2 |  | 8 |  |  | 9-3/4 | 3-1/4 | 54 | 275 |
| CHX 1000 | ADB 1000 | 28-3/4 | 39 | 33 | 21-5/8 | 36-5/8 | 20-5/8 |  | 10 | 2-1/2 | 34 | 10-7/8 | 7-1/4 | 64 | 300 |
| CHX 1500 | ADB 1500 | 34-1/4 | 49 | 42 | 19-1/2 | 46 | 20 | 3/4 | 12 |  | 36 | 14 | 3-1/2 | 64 | 350 |

Dimensions are in inches.

*These heights can be increased up to 2" using adjustable feet.

RATE OF FLOW AND PRESSURE DROP

ADB WITH CHX

| ADB/CHX MODEL | 20˚F T |  | 30˚F T |  | 40˚F T |  | MAX. FLOW |  |  | MIN. FLOW |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | GPM | P | GPM | P | GPM | P | GPM | P | T | GPM | P | T |
| 500 | 49 | 4.5 | 32 | 2.3 | N/A | N/A | 84 | 11.5 | 12˚F | 30 | 2.1 | 32˚F |
| 750 | 73 | 10.0 | 49 | 5.2 | 36 | 3.5 | 110 | 22.1 | 13˚F | 32 | 2.4 | 45˚F |
| 1000 | 97 | 20.7 | 65 | 10.3 | 49 | 6.8 | 110 | 26 | 18˚F | 42 | 5.2 | 46˚F |
| 1500 | N/A | N/A | 97 | 26.6 | 73 | 15.8 | 126 | 41.8 | 23˚F | 73 | 15.8 | 41˚F |

CHX

| MODEL 500 | GPM | 30 | 33 | 42 | 52 | 84 |
| --- | --- | --- | --- | --- | --- | --- |
|  | P (Ft.) | 0.5 | 0.6 | 0.9 | 1.1 | 2.7 |

| MODEL 750 | GPM | 32 | 37 | 42 | 50 | 63 | 77 | 110 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | P (Ft.) | 0.6 | 1.2 | 1.3 | 1.4 | 1.8 | 2.5 | 5.1 |

| MODEL 1000 | GPM | 42 | 51 | 56 | 66 | 84 | 97 | 110 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | P (Ft.) | 1.1 | 1.6 | 1.8 | 2.8 | 4.4 | 5.1 | 6.0 |

| MODEL 1500 | GPM | 73 | 97 | 126 |
| --- | --- | --- | --- | --- |
|  | P (Ft.) | 4.8 | 6.0 | 9.4 |

Ratings based on Natural gas and Propane gas.

Natural gas pressure recommended to be between 7 & 14” w.c.

Propane gas pressure recommended to be between 11 & 14” w.c.

Raypak, Inc., 31111 Agoura Road, Westlake Village, CA 91361-4699 (818) 889-1500 FAX: (818) 889-4522

Raypak Canada LTD., 2805 Slough Street, Mississauga, Ontario, Canada/L4T 1G2 (905) 677-7999 FAX: (905) 677-8036

Raypak Australia Pty. Ltd, 7 Geddes Street, Mulgrave, Victoria, Australia 3170 (6139) 560 4944 FAX: (6139) 560 4974

www.raypak.com

Litho in U.S.A.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com