Job:

# Raytherm® - Type H

## Hydronic Heating Boilers
Commercial

Models 962-1826 (Indoor)

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:

EFFICIENT

- 82% efficiency – highest of any atmospheric

- boiler available today

THERMAL SHOCK PROOF

- Twenty-year warranty against thermal shock damage
up to 150°F differential

- Maximum operating temperature: 230°F

LIGHTWEIGHT

- A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

- Cuts fuel costs substantially because the standby and
radiation losses normal to other boilers are eliminated

LOW WATER OPERATING TEMPERATURE

Proudly Assembled in the USA

Operates with inlet water temperature as low as 105°F
without condensing

#### Heat Exchanger

- ASME Inspected and Stamped
160 PSIG

- National Board Listed

- Headers

Glass-lined Cast Iron – Standard

Bronze – Option A-1

- Finned Tubing

Copper – Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone O-Rings

- 60 PSIG ASME Pressure Relief Valve

- Temperature and Pressure Gauge

- Water Connections

Left Hand – Standard

Right Hand – Option A-6

- Flow Configuration

Two-pass – Standard

Single-pass – Cast Iron Only

- Pump - Rear-mounted, 1/2 HP (Optional)

4.25” Impeller

4.7” Impeller

#### Controls

- 120V, 60Hz, 1 Ph Power Supply

- 120/24V Transformer

- 100% Pilot Shut-off/Lockout

- Electronic, Intermittent Ignition (IID) Pilot

- High Limit Control, Manual Reset, 240°F

- On/Off Switch

#### Controls (cont.)

- Flow Switch

- Economaster Pump Time Delay

#### Gas Train

- Manual Main Gas Shut-off Cock

- Main Gas Pressure Regulator

- Redundant Safety Shut-off Valve

- Control Valve

- Firing Mode

On/off (H4)

Two-stage Firing (H3)

Four-stage Firing (H9)

Mechanical Modulation,
110-170°F (H5)

Mechanical Modulation, 
150-210°F (H1)

Motorized Modulation (H2)

- Fuel

Natural Gas

Propane Gas

- Design Certified ANSI Z21.13/CSA 4.9

#### Construction

- CSA Low Lead Certified (≤ .25% Lead)

- Front Controls

- Stainless Steel Burners

- Polytuf Powder Coat Finish

- Vent Selection

Draft Diverter – Option D-10

Power Vent, Loose – Option D-2

- Base (Optional)

Combustible Floor Shield – 
Option J-1

#### Temperature Controllers

- Note:  H1 and H5 require a system controller

B-6	Two-stage-Mechanical (H3)

B-35	4-20 mA (H2)

B-  	TempTracker Mod+ Hybrid 2-16 Boilers (All)

B-40	Motorized Modulation (H2)

B-41	Motorized Modulation, Outdoor Reset (H2)

B-  	Two-stage Digital (H3)

B-  	Four-stage Digital (H9)

B-60	Stage Interface (H3/H9)

#### Additional Safety Controls

F-9	Low Water Cut-off Probe

I-1	High Limit Control, Auto Reset, 240°F

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

#### Regulatory Agency Requirements

Raytherm - Type H

Hydronic Heating Boilers	Model

MODELS 962 THRU 1826

|  |  |  |  | Dimensions (Inches) |  |  |  |  |  |  |  |  | Approx. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | MBTUH |  |  | Overall | Jacket |  | Gas | Water |  | Flue |  | Shipping |  |
|  | Model | Natural Gas |  | Width | Height | Height |  | Conn. | Conns. |  | Dia. |  | Weight |  |
|  | Size | Input | Output | A | B | C |  | G | H | J | K | L | (Lbs.) |  |
|  | H-962 | 961.7 | 788.6 | 52-3/8 | 76-1/8 (a) | 33-1/2 |  | 1 | 2-1/2 (c) | 23-5/8 | 14 | 28 | 705 |  |
|  | H-1125 | 1124.7 | 922.0 | 59-1/4 | 78-1/8 (a) | 33-1/2 |  | 1 (b) | 2-1/2 (c) | 23-5/8 | 16 | 32 | 745 |  |
|  | H-1223 | 1222.5 | 1002.4 | 63-5/8 | 78-1/8 (a) | 33-1/2 |  | 1 (b) | 2-1/2 (c) | 23-5/8 | 16 | 32 | 805 |  |
|  | H-1336 | 1336.6 | 1096.0 | 68-5/8 | 80-1/8 (a) | 33-1/2 |  | 1-1/4 | 2-1/2 (c) | 23-5/8 | 18 | 36 | 875 |  |
|  | H-1468 | 1467.0 | 1203.0 | 74-7/8 | 80-1/8 (a) | 33-1/2 |  | 1-1/4 | 2-1/2 (c) | 23-5/8 | 18 | 36 | 945 |  |
|  | H-1631 | 1630.0 | 1336.6 | 81-1/8 | 83-1/8 (a) | 36-1/2 |  | 1-1/4 | 2-1/2 (c) | 23-5/8 | 18 | 36 | 985 |  |
|  | H-1826 | 1825.6 | 1497.0 | 89-3/8 | 85-1/8 (a) | 36-1/2 |  | 1-1/4 | 2-1/2 (c) | 23-5/8 | 20 | 40 | 1035 |  |
| - NOTE: Ratings shown are for elevations up to 2,000 feet. For elevations over 2,000, reduce ratings at the rate of 4% for each 1,000 feet above sea level. |  |  |  |  |  |  | - (a) Add 1-1/8" to overall height for combustible floor shield option (b) 1" or 1-1/4" contingent on boiler type or code requirements (c) 3" NPT on single-pass option - (d) Propane input/output is 92% of standard values |  |  |  |  |  |  |  |

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

BOILER RATE OF FLOW AND PRESSURE DROP

|  | Model No. | 10º ΔT |  | 20º ΔT |  |  | 30º ΔT |  | 40º ΔT |  | Minimum Flow |  |  | Maximum Flow |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | GPM | ΔP FT | GPM |  | ΔP FT | GPM | ΔP FT | GPM | ΔP FT | GPM | ΔP FT | ΔT | GPM | ΔP FT | ΔT |
| TWO-PASS | H-962 |  |  | 80 |  | 8.8 | 53 | 3.8 | 40 | 2.2 | 40 | 2.2 | 38 | 90 | 11.0 | 18 |
|  | H-1125 |  |  | 90 |  | 12.0 | 61 | 5.5 | 47 | 3.3 | 45 | 3.1 | 40 | 90 | 12.0 | 21 |
|  | H-1223 | Exceeds Maximum Flow |  |  |  |  | 76 | 7.0 | 51 | 4.0 | 51 | 4.0 | 40 | 90 | 12.5 | 22 |
|  | H-1336 |  |  |  |  |  | 73 | 8.6 | 55 | 4.9 | 55 | 4.9 | 40 | 90 | 13.2 | 25 |
|  | H-1468 |  |  |  |  |  | 80 | 11.0 | 61 | 6.4 | 61 | 6.4 | 40 | 90 | 14.0 | 27 |
|  | H-1631 |  |  |  |  |  | 90 | 14.8 | 68 | 8.3 | 68 | 8.3 | 40 | 90 | 8.3 | 30 |
|  | H-1826 |  |  |  |  |  |  |  | 76 | 10.8 | 76 | 10.8 | 40 | 90 | 15.4 | 34 |
| ONE-PASS | H-962 | 157 | 6.1 |  |  |  | Less than Minimum Flow |  |  |  | 90 | 2.1 | 18 | 200 | 9.7 | 8 |
|  | H-1125 | 184 | 8.8 | 92 | 2.3 |  |  |  |  |  | 90 | 2.3 | 20 | 200 | 10.3 | 9 |
|  | H-1223 | 200 | 11.0 | 100 | 2.9 |  |  |  |  |  | 90 | 2.4 | 22 | 200 | 11.0 | 10 |
|  | H-1336 |  |  | 110 | 3.7 |  |  |  |  |  | 90 | 2.5 | 24 | 200 | 11.7 | 11 |
|  | H-1468 |  |  | 120 | 4.5 |  |  |  |  |  | 90 | 2.7 | 27 | 200 | 12.2 | 12 |
|  | H-1631 |  |  | 134 | 6.0 |  |  |  |  |  | 90 | 2.8 | 30 | 200 | 13.0 | 13 |
|  | H-1826 |  |  | 150 | 8.0 |  | 100 | 3.7 |  |  | 90 | 3.0 | 33 | 200 | 14.7 | 15 |

NOTES:

- Values represent maximum flows and pressure drops for closed heating systems

- Maximum acceptable flow through heat exchanger tubes is 90 GPM (two-pass); 200 GPM (one-pass)

- Single-pass heat exchangers are to be used only when flow rates exceed the allowable for two-pass