Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

- 100% Factory Fire Tested

- Efficiency: 87%

- Maximum Outlet Temperature: 230°F

- Minimum Non-Condensing Inlet Temperature: 120°F

- Thermal Shock Proof Heat Exchanger

- Limited Twenty-Year Thermal Shock Warranty

- Limited Ten-Year Closed-System Heat Exchanger Warranty

- Diagnostic Center with Fault History

- PolyTuf Powder Coated Cabinet

- No Combustible Floor Shield Required

- Fan-Assisted

- Patented Burner Security Blanket

#### Heat Exchanger

H Stamp

Headers

Glass-Lined Cast Iron – Standard

Brass – Option A-1

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone High Temp. O-Rings

ASME Pressure Relief Valve

60 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

Right – Option A-6

#### Controls

120V, 60Hz, 1( Power Supply

120/24V 60Hz Transformer

100% Shut-Off/Lockout

Hot Surface Ignition

Remote Flame Sensor

High Limit Control, Manual Reset

On/Off Power Switch

Manual Shut-Off, Front-Mounted

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switches

Economaster Pump Time Delay

Enable/Disable

Diagnostics Panel with LCD Display

2 Lines, 20 Characters

#### Gas Train

Manual Gas Shut-Off Valve(s)

Combo Valve(s)

Low Gas Pressure Switch, Manual

Firing Mode

3-Stage (H8): Model 992BE

4-Stage (H9): Models 1262BE -2342BE

Fuel

Natural Gas

Propane Gas

Design Certified ANSI Z21.13/
CSA 4.9

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

CSA Low Lead Certified (≤ .25 Pb)

#### Venting

Vent Location

Top – Standard

Rear – Option D-14

Vent Termination Cap

Outdoor  D-11

Indoor, Horizontal  D-15

Indoor, Vertical (by others)

Combustion Air

In-Line Filter Kit (TruSeal only)
D-17

Air Intake Elbow  D-16

Extractor – Optional

By others

Not required

#### Burner

Ultra-Low NOx: Less than 20 PPM

#### Temperature Controls

B-  	TempTracker Digital Controller, 2-Stage

B-  	TempTracker Digital Controller, 4-Stage

B-  	TempTracker Mod+ Hybrid (2-16 Boilers)

B-60	Stage Interface

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1(, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Start (See 2000.49)

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

#### Regulatory Agency Requirements

#### Hi Delta – Type H

Models 992BE-2342BE, 87% Efficiency	Model

# Text boxes

# Hi Delta® - Type H

## Hydronic Heating Boiler Models 992BE-2342BE

## 87% Efficiency

Proudly Made in the USA

Patent No. 7,044,124

For Metric information, see Catalog

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

2.	Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 – 13” WC.

NOTE:  Pump location varies based on model and application.

SPECIFICATIONS

|  |  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH | Firing | A | H | K | T | W | Amp. | Shipping |
| Model | Input | Output | Stages | Width | NPT |  |  |  | Draw* | Wt. (Lbs.) |
| 992BE | 990 | 861 | 3 | 57-1/8 | 2-1/2 | 10 | 10 | 16-13/16 | <12 | 900 |
| 1262BE | 1260 | 1096 | 4 | 68-1/2 | 2-1/2 | 12 | 10 | 20-9/16 | <12 | 1010 |
| 1532BE | 1530 | 1331 | 4 | 79-7/8 | 2-1/2 | 12 | 10 | 24-3/8 | <12 | 1225 |
| 1802BE | 1800 | 1566 | 4 | 91-1/8 | 2-1/2 | 14 | 10 | 28-1/8 | <12 | 1350 |
| 2002BE | 1999 | 1739 | 4 | 102-1/2 | 2-1/2 | 14 | 10 | 31-15/16 | <12 | 1450 |
| 2072BE | 2070 | 1801 | 4 | 102-1/2 | 2-1/2 | 14 | 10 | 31-15/16 | <12 | 1450 |
| 2342BE | 2340 | 2036 | 4 | 113-7/8 | 2-1/2 | 16 | 10 | 35-11/16 | <12 | 1520 |

Dimensions are in inches.	* Without pump

RATES OF FLOW AND PRESSURE DROPS

|  | 20°F ∆T | 30°F ∆T | Min. Flow | Max. Flow |
| --- | --- | --- | --- | --- |
| Model | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) | ∆T | GPM | ∆P (ft) | ∆T |
| 992BE | 86 | 6.0 | 57 | 2.7 | 43 | 1.6 | 40 | 132 | 14.0 | 13 |
| 1262BE | 110 | 10.7 | 73 | 4.9 | 55 | 2.8 | 40 | 132 | 15.5 | 17 |
| 1532BE | 132 | 16.5 | 89 | 7.6 | 67 | 4.4 | 40 | 132 | 16.5 | 20 |
| 1802BE | N/A | N/A | 104 | 11.6 | 78 | 6.5 | 40 | 132 | 18.0 | 24 |
| 2002BE | N/A | N/A | 116 | 15.1 | 87 | 8.7 | 40 | 132 | 19.5 | 26 |
| 2072BE | N/A | N/A | 120 | 16.2 | 90 | 9.3 | 40 | 132 | 19.5 | 27 |
| 2342BE | N/A | N/A | N/A | N/A | 102 | 13.0 | 40 | 132 | 21.0 | 31 |

Basis is 30 GPM or 40°F ∆T for minimum flow, 132 GPM for maximum flow.

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com