# Hi Delta® FlexGas® - Type WH

## Dual-Fuel Water Heaters 
Models 992BD-2342BD

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:	       	 	MBTUH Input:

Fast, Economical Natural-to-Propane Gas Switchover

100% Factory Fire Tested

Efficiency: 85%

Maximum Outlet Temperature: 200°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Five-Year Thermal Shock Warranty

Limited Five-Year Heat Exchanger Warranty

Patent Nos. 6,904,873 & 7,044,124; other patents pending

Diagnostic Center with Fault History

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Proudly Assembled in the USA

Fan-Assisted

Patented Burner Security Blanket

#### Heat Exchanger

HLW Stamp

Headers

Bronze – Standard

Glass-Lined Cast Iron – 
Option A-2

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone High Temp. O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

A6 – 150 PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

Right – Option A-6

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

100% Shut-Off/Lockout

Hot Surface Ignition

Remote Flame Sensor

High Limit Control, Manual Reset

On/Off Power Switch

Manual Shut-Off, Front-Mounted

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switches

Economaster Pump Time Delay

Enable/Disable

#### Gas Train

Manual Gas Shut-Off Valve(s)

Low Gas Pressure Switch - Manual

Safety Shut-Off Valve

Firing Control Valve

Firing Mode

3-Stage: Model 992BD

4-Stage: Models 1262BD -
2342BD

Natural/Propane Gas

Gas Connection

Left – Standard

Right – Option Z-1

Design Certified - ANSI Z21.10.3/
CSA 4.3

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

CSA Low Lead Certified ≤ .25% Lead

#### Venting

Vent Location

Top – Standard

Rear – Option D-14

Vent Termination Cap

Outdoor  D-11

Indoor, Horizontal  D-15

Indoor, Vertical (by others)

Combustion Air

In-Line Filter Kit (TruSeal 
only)  D-17

Air Intake Elbow  D-16

Extractor – Optional

By others

Not required

#### Burner

Ultra-Low NOx: Less than 20 PPM

#### Temperature Controls

B-2	Tankstat, Single-Stage (100-200°F)

B-3	Tankstat, 2-Stage (100-200°F)

B-21	TempTracker Digital Controller, 
4-Stage

B-26	TempTracker Digital Controller, 
2-Stage (Mtd)

B-         TempTracker Mod+ Hybrid,
          (up to 16 heaters)

B-60	Stage Interface Card

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1, 60Hz Water Hardness:       GPG

Bronze
 Mounted	 Loose

Front	 Rear

P-      Cold Water Run (See 1000.19)

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

For Metric information, see Catalog

#### Regulatory Agency Requirements

For Metric information, see Catalog

For Metric information, see Catalog

For Metric information, see Catalog

#### Hi Delta FlexGas – Type WH
Models 992BD-2342BD	Model

NOTE:  Pump location varies based on model and application.

NOTES

1.	Dimensions are in inches

2.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

3.	Required natural gas supply pressure is 
7 - 10.5” WC. Required propane gas supply pressure is 11 - 13” WC.

SPECIFICATIONS

| Model | MBTUH |  | Firing Stages | A Width | B | K | T | W | Amp Draw* | Approx. Shipping Wt. (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output |  |  |  |  |  |  |  |  |
| 992BD | 990 | 842 | 3 | 57-1/8 | 41-3/8 | 10 | 10 | 16-13/16 | <12 | 930 |
| 1262BD | 1260 | 1071 | 4 | 68-1/2 | 41-1/2 | 12 | 10 | 20-9/16 | <12 | 1040 |
| 1532BD | 1530 | 1301 | 4 | 79-7/8 | 36 | 12 | 10 | 24-3/8 | <12 | 1255 |
| 1802BD | 1800 | 1530 | 4 | 91-1/8 | 33-1/2 | 14 | 10 | 28-1/8 | <12 | 1380 |
| 2072BD | 2070 | 1760 | 4 | 102-1/2 | 39 | 14 | 10 | 31-15/16 | <12 | 1480 |
| 2342BD | 2340 | 1989 | 4 | 113-7/8 | 34 | 16 | 10 | 35-11/16 | <12 | 1550 |

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

*Without Pump

| Model | RATES OF FLOW AND PRESSURE DROPS |  |  |  |  |  |  |  |  |  | RECOVERY RATES (GPH) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20ºT ΔT |  | 30ºT ΔT |  | Min. Flow |  |  | Max. Flow |  |  | Temperature Rise (ºF) |  |  |  |  |  |  |  |  |
|  | GPM | ΔP (ft.) | GPM | ΔP (ft.) | GPM | ΔP (ft.) | ΔT | GPM | ΔP (ft.) | ΔT | 20º | 30º | 40º | 50º | 60º | 70º | 80º | 90º | 100º |
| 992BD | 85 | 5.7 | N/A | N/A | 60 | 2.7 | 28 | 132 | 13.1 | 13 | 5100 | 3400 | 2550 | 2040 | 1700 | 1457 | 1275 | 1133 | 1020 |
| 1262BD | 107 | 10.2 | 71 | 4.4 | 71 | 4.4 | 30 | 132 | 14.8 | 16 | 6491 | 4327 | 3245 | 2596 | 2164 | 1855 | 1623 | 1442 | 1298 |
| 1532BD | 130 | 16.2 | 87 | 7.2 | 87 | 7.2 | 30 | 132 | 16.5 | 20 | 7882 | 5255 | 3941 | 3153 | 2627 | 2252 | 1970 | 1752 | 1576 |
| 1802BD | N/A | N/A | 103 | 11.0 | 102 | 10.8 | 30 | 132 | 18.3 | 23 | 9273 | 6182 | 4636 | 3709 | 3091 | 2649 | 2318 | 2061 | 1855 |
| 2072BD | N/A | N/A | 118 | 15.3 | 117 | 15.0 | 30 | 132 | 19.0 | 27 | 10664 | 7109 | 5332 | 4265 | 3555 | 3047 | 2666 | 2370 | 2133 |
| 2342BD | N/A | N/A | 132 | 21.0 | 132 | 21.4 | 30 | 132 | 21.4 | 30 | 12055 | 8036 | 6027 | 4822 | 4018 | 3444 | 3014 | 2679 | 2411 |

Basis is 60 GPM or 30ºF ΔT for minimum flow, 132 GPM for maximum flow.