Job:

# Raytherm® - Type WH

## Water Heaters
Commercial

Models 962-1826 (Indoor)

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:

EFFICIENT

- 82% thermal efficiency – highest of any atmospheric

- water heater available today

THERMAL SHOCK PROOF

- Twenty-year warranty against thermal shock damage
up to 150°F differential

- Maximum outlet temperature: 210°F

LIGHTWEIGHT

- A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

- Cuts fuel costs substantially because the standby and
radiation losses associated with tank-type
water heaters are eliminated

LOW WATER OPERATING TEMPERATURE

Proudly Assembled in the USA

- Operates with water temperature as low as 105°F
without condensing

#### Heat Exchanger

- ASME Inspected and Stamped
160 PSIG

- National Board Approved

- Headers

Bronze – Standard

Glass-lined Cast Iron – Option A-2

- Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone O-Rings

- 125 PSIG ASME Pressure Relief Valve

- Temperature and Pressure Gauge

- Water Connections

Left Hand – Standard

Right Hand – Option A-6

- Two-pass Flow Configuration

- Pump, Rear-mounted, 1/2 HP, 
120 VAC, 1 60 Hz – Optional

4.25” Impeller

4.7” Impeller

#### Controls

- 120V, 60Hz, 1 Ph Power Supply

- 120/24V Transformer

- 100% Pilot Shut-off/Lockout

- Electronic, Intermittent Ignition (IID) Pilot

#### Controls (cont.)

- High Limit Control, Manual Reset –  
200°F

- On/Off Switch

- Flow Switch

- Economaster II Pump Time Delay

#### Gas Control Train

- Manual Main Gas Shut-off Cock

- Main Gas Pressure Regulator

- Redundant Safety Shut-off Valve

- Control Valve

- Firing Mode

On/Off

2-stage Firing

Mechanical Modulation

- Fuel

Natural Gas

Propane Gas

- Design Certified ANSI Z21.10.3

#### Construction

- Front Controls

- Stainless Steel Burners

- PolyTuf Powder Coat Finish

- Vent Selection

Drafthood – Option D-10

Motorized Draft Inducer – 
Option D-2

- Base – Optional

Combustible Floor Shield – 
Option J-1

- CSA Low Lead Certified ≤ .25% Lead

#### Temperature Controls

B-2	Single-Stage Tankstat 
(100-180°F)

B-3	2-Stage Tankstat (100-180°F)

B-26	2-Stage Digital

B-21	4-Stage Digital

#### Additional Safety Controls

F-9	Low Water Cut-off Probe

I-3	High Limit Control, Auto Reset, 180°F

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

#### Regulatory Agency Requirements

Raytherm - Type WH

Models 962-1826	Model

| Electrical Requirements 120 VAC |  |  |
| --- | --- | --- |
| Model | With Pump | W/O Pump |
| 962-1826 | < 10 Amps | < 4 Amps |

MODELS 962 THRU 1826

|  |  |  | Dimensions (Inches) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | MBTUH |  |  | Overall | Jacket | Gas | Water |  | Flue |  | Shipping Weight |  |
| No. | Natural Gas |  | Width | Height | Height | Conn. | Conns. |  | Dia. |  | Lbs. (Approx.) |  |
|  | Input | Output | A | B | C | G | H | J | K | L | Less Pump | w/Pump |
| WH-962 | 961.7 | 788.6 | 52-3/8 | 76-1/8 | 33-1/2 | 1 | 2-1/2 | 23-5/8 | 14 | 28 | 705 | 760 |
| WH-1125 | 1124.7 | 922.0 | 59-1/4 | 78-1/8 | 33-1/2 | 1 | 2-1/2 | 23-5/8 | 16 | 32 | 745 | 800 |
| WH-1223 | 1222.5 | 1002.4 | 63-5/8 | 78-1/8 | 33-1/2 | 1-1/4 | 2-1/2 | 23-5/8 | 16 | 32 | 805 | 860 |
| WH-1336 | 1336.6 | 1096.0 | 68-5/8 | 80-1/8 | 33-1/2 | 1-1/4 | 2-1/2 | 23-5/8 | 18 | 36 | 875 | 930 |
| WH-1468 | 1467.0 | 1203.0 | 74-7/8 | 80-1/8 | 33-1/2 | 1-1/4 | 2-1/2 | 23-5/8 | 18 | 36 | 945 | 1000 |
| WH-1631 | 1630.0 | 1336.6 | 81-1/8 | 83-1/8 | 36-1/2 | 1-1/4 | 2-1/2 | 23-5/8 | 18 | 36 | 985 | 1040 |
| WH-1826 | 1825.6 | 1497.0 | 89-3/8 | 85-1/8 | 36-1/2 | 1-1/4 | 2-1/2 | 23-5/8 | 20 | 40 | 1035 | 1090 |

NOTES:	Ratings are shown for elevations up to 2,000 feet. For elevations over 2,000 feet, reduce ratings 4% for each 1,000 feet above sea level.

HEATER RECOVERY RATES (GPH)

| Model No. | Temperature Rise |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20°F | 30°F | 40°F | 50°F | 60°F | 80°F | 100°F |
| WH-962 | 4733 | 3156 | 2367 | 1893 | 1578 | 1183 | 947 |
| WH-1125 | 5536 | 3690 | 2768 | 2214 | 1845 | 1384 | 1107 |
| WH-1223 | 6017 | 4011 | 3009 | 2407 | 2006 | 11504 | 1203 |
| WH-1336 | 6579 | 4386 | 3289 | 2631 | 2193 | 1645 | 1316 |
| WH-1468 | 7221 | 4818 | 3610 | 2888 | 2407 | 1805 | 1444 |
| WH-1631 | 8023 | 5349 | 4011 | 3209 | 2674 | 2006 | 1605 |
| WH-1826 | 8986 | 5990 | 4493 | 3594 | 2995 | 2246 | 1797 |

HEATER RATES OF FLOW AND PRESSURE DROPS

| Model No. | 20° T |  | 30° T |  | 40° T |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | GPM | P (ft) | GPM | P (ft) | GPM | P (ft) |
| WH-962 | 79 | 8.5 | 53 | 3.8 | N/A | N/A |
| WH-1125 | N/A | N/A | 61 | 5.5 | 46 | 3.1 |
| WH-1223 | N/A | N/A | 67 | 7.0 | 50 | 3.9 |
| WH-1336 | N/A | N/A | 73 | 8.6 | 55 | 4.9 |
| WH-1468 | N/A | N/A | 80 | 11.0 | 60 | 6.2 |
| WH-1631 | N/A | N/A | 90 | 14.8 | 67 | 8.0 |
| WH-1826 | N/A | N/A | N/A | N/A | 75 | 10.6 |

NOTE:	Maximum acceptable flow through heat exchanger tubes is 90GPM.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com