Job:

# Raytherm® - Type WH

## Water Heaters
Commercial

Models 926-1758 (Outdoor)

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:

EFFICIENT

82% thermal efficiency – highest of any atmospheric water heater available today

OUTDOOR

THERMAL SHOCK PROOF

- Twenty-year warranty against thermal shock damage up to 150°F differential

- Maximum operating temperature: 210°F

LIGHTWEIGHT

- A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

- Cuts fuel costs substantially because the standby and radiation losses associated with tank-type water heaters are eliminated

LOW WATER OPERATING TEMPERATURE

- Operates with water temperature as low as
105°F without condensing

#### Heat Exchanger

- ASME Inspected and Stamped
160 PSIG

- National Board Approved

- Headers

Bronze – Standard

Glass-lined Cast Iron – Option A-2

- Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone O-Rings

- 125 PSIG ASME Pressure Relief Valve

- Temperature and Pressure Gauge

- Water Connections

Left Hand – Standard

Right Hand – Option A-6

- Two-pass Flow Configuration

- Pump, Rear-mounted, 1/2 HP, 
120 VAC, 1 60 Hz – Optional

4.25” Impeller

4.7” Impeller

#### Controls

- 120V, 60Hz, 1 Ph Power Supply

- 120/24V Transformer

- 100% Pilot Shut-off/Lockout

- Electronic, Intermittent Ignition (IID) Pilot

- High Limit Control, Manual Reset – 200°F

#### Controls (cont.)

- On/Off Switch

- Flow Switch

- Economaster II Pump Time Delay

#### Gas Control Train

- Manual Main Gas Shut-off Cock

- Main Gas Pressure Regulator

- Redundant Safety Shut-off Valve

- Control Valve

- Firing Mode

On/Off (WH1)

2-stage Firing (WH3)

Mechanical Modulation (WH2)

- Fuel

Natural Gas

Propane Gas

- Design Certified ANSI Z21.10.3/
CSA 4.3

#### Construction

- Front Controls

- Stainless Steel Burners

- PolyTuf Powder Coat Finish

- Stackless Top

- Base – Optional

Combustible Floor Shield – 
Option J-1

- CSA Low Lead Certified ≤ .25 Pb

#### Temperature Controls

B-2	Single-Stage Tankstat 
(100-180°F)

B-3	2-Stage Tankstat (100-180°F)

B-26	2-Stage Digital

B-21	4-Stage Digital

#### Additional Safety Controls

F-9	Low Water Cut-off Probe

I-3	High Limit Control, Auto Reset, 180°F

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

#### Regulatory Agency Requirements

Raytherm - Type WH

Models 926-1758	Model

HEATER RECOVERY RATES (GPH)

| Model | Temperature Rise |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | 20°F | 30°F | 40°F | 50°F | 60°F | 80°F | 100°F |
| WH-926 | 4558 | 3038 | 2279 | 1823 | 1519 | 1139 | 912 |
| WH-1083 | 5330 | 3554 | 2665 | 2132 | 1777 | 1333 | 1066 |
| WH-1178 | 5798 | 3865 | 2899 | 2319 | 1933 | 1450 | 1160 |
| WH-1287 | 6335 | 4223 | 3167 | 2534 | 2112 | 1584 | 1267 |
| WH-1414 | 6955 | 4636 | 3477 | 2782 | 2318 | 1739 | 1391 |
| WH-1571 | 7727 | 5152 | 3864 | 3091 | 2576 | 1932 | 1545 |
| WH-1758 | 8653 | 5769 | 4326 | 3461 | 2884 | 2163 | 1731 |

HEATER RATES OF FLOW AND PRESSURE DROPS

| Model | 20° T |  | 30° T |  | 40° T |  |
| --- | --- | --- | --- | --- | --- | --- |
| No. | GPM | P (ft) | GPM | P (ft) | GPM | P (ft) |
| WH-926 | 76 | 8.0 | 51 | 3.5 | N/A | N/A |
| WH-1083 | 89 | 11.7 | 59 | 5.1 | 44 | 2.9 |
| WH-1178 | N/A | N/A | 64 | 6.3 | 48 | 3.6 |
| WH-1287 | N/A | N/A | 70 | 8.0 | 53 | 4.5 |
| WH-1414 | N/A | N/A | 77 | 10.2 | 58 | 5.8 |
| WH-1571 | N/A | N/A | 86 | 13.2 | 64 | 7.3 |
| WH-1758 | N/A | N/A | N/A | N/A | 72 | 9.7 |

NOTE:	Maximum acceptable flow through heat exchanger tubes 
is 90GPM.

MODELS 926 THRU 1758

|  |  |  | Dimensions (Inches) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Model | MBTUH |  |  | Gas | Water | Shipping Weight |  |
| No. | Natural Gas |  | Width | Conn. | Conns. | Lbs. (Approx.) |  |
|  | Input | Output | A | G | H | Less Pump | w/Pump |
| WH-926 | 926.0 | 759.0 | 52-3/8 | 1 | 2-1/2 | 785 | 840 |
| WH-1083 | 1083.0 | 888.0 | 59-1/4 | 1 | 2-1/2 | 865 | 920 |
| WH-1178 | 1178.0 | 966.0 | 63-5/8 | 1 | 2-1/2 | 925 | 980 |
| WH-1287 | 1287.0 | 1055.0 | 68-5/8 | 1-1/4 | 2-1/2 | 980 | 1035 |
| WH-1414 | 1413.0 | 1158.5 | 74-7/8 | 1-1/4 | 2-1/2 | 1080 | 1130 |
| WH-1571 | 1570.0 | 1287.0 | 81-1/8 | 1-1/4 | 2-1/2 | 1130 | 1190 |
| WH-1758 | 1758.0 | 1441.5 | 89-3/8 | 1-1/4 | 2-1/2 | 1160 | 1220 |

NOTE:	Ratings shown are for elevations up to 2,000 feet. For elevations over 2,000 feet, reduce ratings 4% for each 1,000 feet above sea level.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com