Job:

# Hi Delta - Type H

## Space Heating/Hot Water Boilers Models 992B-2342B

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

- 100% Factory Fire Tested

- Efficiency: 84%

- Maximum Outlet Temperature: 230°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal Shock Proof Heat Exchanger

- Limited Twenty-Year Thermal Shock Warranty

- Limited Ten-Year Closed-System Heat Exchanger Warranty

- Full Safety Diagnostics with Fault History

- PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Patent No. 7,044,124

Proudly Assembled in the USA

Fan-Assisted

- Patented Burner Security Blanket

#### Heat Exchanger

- H Stamp

- Headers

Glass-Lined Cast Iron – Standard

Brass – Option A-1

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone High Temp. O-Rings

- ASME Pressure Relief Valve

60 PSIG – Standard

PSIG – Optional

- Temperature and Pressure Gauge

- Water Connections

Left – Standard

Right – Option A-6

#### Controls

- 120V, 60Hz, 1 Power Supply

- 120/24V 60Hz Transformer

- 100% Shut-Off/Lockout

- Hot Surface Ignition

- Remote Flame Sensor

- High Limit Control, Manual Reset

- On/Off Power Switch

- Manual Shut-Off, Front-Mounted

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switches

- Economaster Pump Time Delay

- Enable/Disable

- Diagnostics Panel with LCD Display, 2 Lines 20 Characters

#### Gas Train

- Manual Gas Shut-Off Valve(s)

- Combo Valve(s)

- Low Gas Pressure Switch, Manual

- Firing Mode

3-Stage (H8): Model 992B

4-Stage (H9): Models 
1262B-2342B

- Fuel

Natural Gas

Propane Gas

4” WC Gas Supply Pressure 
G-20

- Design Certified ANSI Z21.13/
CSA 4.9

#### Construction

- Indoor/Outdoor Construction

- Enclosed Front Controls

- CSA Low Lead Certified (≤ .25%

- Lead)

#### Venting

- Vent Location

Top – Standard

Rear – Option D-14

- Vent Termination Cap

Outdoor  D-11

Indoor, Horizontal  D-15

Indoor, Vertical (by others)

- Combustion Air

In-Line Filter Kit (TruSeal only)
D-17

Air Intake Elbow  D-16

- Extractor – Optional

By others

Not required

#### Burner

- Ultra-Low NOx: Less than 20 PPM

#### Temperature Controls

B-  	TempTracker Digital Controller, 2-Stage

B-  	TempTracker Digital Controller, 4-Stage

B-  	TempTracker Mod+ Hybrid (2-16 Boilers)

B-60	Stage Interface

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Start (See 2000.49)

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

#### Regulatory Agency Requirements

For Metric information, see Catalog

#### Hi Delta – Type H

Models 992B-2342B	Model

SPECIFICATIONS

|  |  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH |  | Firing | A | H | K | T | W | Amp. | Shipping |
| Model | Input | Output | Stages | Width | NPT |  |  |  | Draw* | Wt. (Lbs.) |
| 992B | 990 | 832 | 3 | 57-1/8 | 2-1/2 | 10 | 10 | 16-13/16 | <12 | 900 |
| 1262B | 1260 | 1058 | 4 | 68-1/2 | 2-1/2 | 12 | 10 | 20-9/16 | <12 | 1010 |
| 1532B | 1530 | 1285 | 4 | 79-7/8 | 2-1/2 | 12 | 10 | 24-3/8 | <12 | 1225 |
| 1802B | 1800 | 1512 | 4 | 91-1/8 | 2-1/2 | 14 | 10 | 28-1/8 | <12 | 1350 |
| 2002B | 1999 | 1679 | 4 | 102-1/2 | 2-1/2 | 14 | 10 | 31-15/16 | <12 | 1450 |
| 2072B | 2070 | 1739 | 4 | 102-1/2 | 2-1/2 | 14 | 10 | 31-15/16 | <12 | 1450 |
| 2342B | 2340 | 1966 | 4 | 113-7/8 | 2-1/2 | 16 | 10 | 35-11/16 | <12 | 1520 |

Dimensions are in inches.	* Without pump

RATES OF FLOW AND PRESSURE DROPS

|  | 20°F ∆T |  | 30°F ∆T |  | ###### Min. Flow |  |  | ###### Max. Flow |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | ###### GPM | ∆P (ft) | ###### GPM | ∆P (ft) | ###### GPM | ∆P (ft) | ###### ∆T | ###### GPM | ∆P (ft) | ###### ∆T |
| 992B | 84 | 5.6 | 56 | 2.5 | 42 | 1.5 | 40 | 132 | 14.0 | 13 |
| 1262B | 107 | 10.0 | 71 | 4.5 | 53 | 2.6 | 40 | 132 | 15.5 | 16 |
| 1532B | 130 | 16.0 0 | 86 | 7.1 | 65 | 4.1 | 40 | 132 | 16.5 | 20 |
| 1802B | N/A | N/A | 102 | 10.8 | 76 | 6.0 | 40 | 132 | 18.0 | 23 |
| 2002B | N/A | N/A | 113 | 14.0 | 85 | 8.1 | 40 | 132 | 19.5 | 26 |
| 2072B | N/A | N/A | 117 | 15.0 | 88 | 8.7 | 40 | 132 | 19.5 | 27 |
| 2342B | N/A | N/A | 132 | 21.0 | 99 | 12.0 | 40 | 132 | 21.0 | 30 |

Basis is 30 GPM or 40°F ∆T for minimum flow, 132 GPM for maximum flow.

NOTE:  Pump location varies based on model and application

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

2.	Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com