# MVB® - Type H

## Heating Boilers
Models 503A-2003A

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- 86.2% Thermal Efficiency at Full Rate

- 100% Factory Fire-Tested

- VERSA IC® Integrated Controller with 7” Color Touchscreen Display

- Raymote™ remote connectivity provided standard

- Electronic Modulation, Constant Ratio 7:1 Turndown

- Full Safety Diagnostics with History

- Status Display Lights

- Modbus RTU BMS Port

- Maximum Outlet Water Temperature: 235°F

- Minimum Acceptable Inlet Water Temperature: 120°F

- Limited Twenty-Five-Year Thermal Shock Warranty

Proudly Assembled in the USA

Limited Ten-Year Heat Exchanger Warranty

- Ultra Low NOx – Less than 20PPM

#### Heat Exchanger

Headers

Cast Iron – Standard

A-1 Bronze

ASME H Stamped
160 PSIG MAWP

National Board Approved

Fin Tubing

Copper – Standard

A-3 Cupronickel

ASME Powder-Coated Tube Sheet

Silicone High-Temp O-Rings

ASME Pressure Relief Valve

60 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge,
Shipped Loose

Stainless Steel Evaporator Plate

Four-pass heat exchanger

#### Control

120V, 60Hz, 1Ø, Power Supply

120/24V 60Hz Transformer

VERSA IC® built-in controller

7” color HD touchscreen display

Raymote™ Wi-Fi remote connectivity

Cascade up to 4 Boilers

Ignition Module

3-Try – Standard

C-6 Single-Try

Remote Flame Sensor

Freeze Protection

High Limit, Manual Reset, Fixed, 240ºF

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Pump Outputs

Boiler pump

DHW Indirect – Pilot Duty

System – Pilot Duty

Programmable Pump Time Delays

- Water Temperature Sensors (7)

- Cold Water Protection Function

- Optional Variable Speed Pump

- Optional Proportional Valve

- Modbus RTU BMS Port

- B-85   Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

- B-86   Gateway - LonWorks

#### Burner

Hot Surface Ignition (HSI)

Radially-Fired Knitted Burner

#### Gas Train

Fuel

Natural Gas

Propane (Minimum Grade HD-5)

Dual-Seat Combination Firing Valve

Manual Shut-Off Valve

#### Construction

Design Certified ANSI Z21.13/CSA 4.9

CSA Low Lead Certified ≤.25% Lead

Indoor/Outdoor Construction

Front Controls Enclosed

PolyTuf Powder Coat Finish

Rear Connections (Water, Electrical, Gas, Vent, Combustion Air)

Combustion Air Filter – Inline

#### Venting

Vent Termination

D-11 Outdoor

D-15 Indoor, Horizontal

Indoor, Vertical (by others)

Combustion Air

D-16 Air Intake Elbow

Extractor – Optional

By others

Not required

Options

A-30	Air Vent, Auto, 150 PSI (loose)

B-31	Dry-Well Assembly

B-32	Outdoor Air Sensor

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit, Auto Reset, Adj., 
100-240F

I-2	High Limit, Manual Reset, Adj., 100-240F (additional)

P-  	Pump:      HP, 120V, 1, 60Hz

Cast Iron	 Bronze

Loose	 Mounted

P-  	Cold Water Start

P-  	Cold Water Run

S-1	Low Gas Pressure Switch, 
Manual Reset

S-2	High Gas Pressure Switch, Manual Reset

Z-12	Condensate Treatment Kit

#### Additional Options or Accessories

#### Multi-Boiler Temperature Controllers

TempTracker Mod+ Hybrid

B-36 2-4 Heaters

B-37 5-10 Heaters

B-38 11-16 Heaters

B-39 	EMS 4-20mA Remote Setpoint Interface Module

B-62   BACnet MS/TP Interface

MVB® – Type H

Models 503A-2003A	Model

|  | Certified Minimum | Recomm. Service |
| --- | --- | --- |
| Front | 24” | 24” |
| Rear | 12” | 24” |
| Right | 1’ | 1” |
| Left | 1” | 1” |
| Top | 0” | 10” |
| Floor | 0” | 0” |
| Vent | 1” | 1” |

CLEARANCES

| Model (H7-) | MBTUH |  | Dimensions (in.) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | B Height | D | E | F | G* NPT | H NPT | K Flue Ø | L | M | N C/A Ø | P | R | V |
|  | Input | Output |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 503A | 500 | 431 | 43 | 30-3/4 | 35 | 23-3/4 | 1 | 2 | 6 | 13-3/4 | 14-1/4 | 6 | 36-3/4 | 8-1/4 | 1-3/4 |
| 753A | 750 | 647 | 49 | 36-3/4 | 40-3/4 | 29-1/2 | 1 | 2 | 6 | 13-1/2 | 14-1/4 | 6 | 42-1/2 | 8-1/4 | 1-3/4 |
| 1003A | 999 | 861 | 55 | 42-3/4 | 46-3/4 | 35-1/2 | 1-1/4 | 2-1/2 | 6 | 13-1/2 | 14-1/4 | 6 | 48-1/2 | 8-1/4 | 1-3/4 |
| 1253A | 1250 | 1078 | 61 | 48-3/4 | 53 | 41-3/4 | 1-1/4 | 2-1/2 | 8 | 13-3/4 | 17-1/4 | 8 | 54-3/4 | 8-1/4 | 1-3/4 |
| 1503A | 1500 | 1293 | 67 | 54-3/4 | 58-3/4 | 47-1/2 | 1-1/4 | 2-1/2 | 8 | 13-3/4 | 17-1/4 | 8 | 60-1/2 | 8-1/4 | 1-3/4 |
| 1753A | 1750 | 1508 | 75 | 61 | 65-1/4 | 53-3/4 | 2 | 2-1/2 | 8 | 13-1/2 | 17-1/4 | 8 | 68-1/2 | 9-1/2 | 5 |
| 2003A | 1999 | 1723 | 81 | 66-3/4 | 71-1/4 | 59-1/2 | 2 | 2-1/2 | 8 | 13-3/4 | 17-1/4 | 8 | 74 | 9-1/2 | 5 |

* For natural gas. For propane, 1” NPT for all sizes.

- Ratings shown are for elevations up to 4,500 feet. For installations at elevations above 4,500 feet, please consult the factory for additional instructions.

- For direct vent applications, please contact the factory about relocating the pump.

| PUMP HP (Amps*) |  |  |  |
| --- | --- | --- | --- |
| Model (H7-) | Water Hardness |  |  |
|  | Soft | Medium | Hard |
| 503A | 1/4 - 6 | 1/4 - 6 | 3/4 – 11 |
| 753A | 1/4 - 6 | 1/2 – 7 | 3/4 – 11 |
| 1003A | 1/4 - 6 | 1/2 – 7 | 1 – 14 |
| 1253A | 1/2 – 7 | 1 – 14 | 1 – 14 |
| 1503A | 3/4 – 11 | 1 – 14 | 1 – 14 |
| 1753A | 1 – 14 | 1-1/2 – 16 | 1-1/2 – 16 |
| 2003A | 1 – 14 | 1-1/2 – 16 | 1-1/2 – 16 |

*Current Draw is for Pump Only

MVB® – Type H

Models 503A-2003A	Model

| Model (H7-); Shipping Weight (Lbs.); Footprint (Ft2); Amps*. 503A; 600; 5.4; 12. 753A; 670; 5.4; 12. 1003A; 720; 5.4; 12. 1253A; 780; 5.4; 12. 1503A; 840; 5.4; 12. 1753A; 940; 5.4; 18. 2003A; 1000; 5.4; 18. *Current draw is for heater only. (Supply breaker must have delayed trip.) |  |
| --- | --- |

RATES OF FLOW AND PRESSURE DROPS

| Model (H7-) | 20°F ΔT |  | 30°F ΔT |  | 39°F ΔT* |  | Maximum Flow |  |  | Minimum Flow* |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | GPM | ΔP (ft.) | GPM | ΔP (ft.) | GPM | ΔP (ft.) | GPM | ΔP (ft.) | ΔT (°F) | GPM | ΔP (ft.) | ΔT (°F) |
| 503A | 43 | 2.8 | 29 | 1.4 | N/A | N/A | 100 | 11.3 | 8.6 | 25 | 1.1 | 35 |
| 753A | 65 | 6.4 | 43 | 3.1 | 33 | 1.9 | 100 | 13.8 | 13 | 33 | 1.9 | 39 |
| 1003A | 86 | 12.0 | 57 | 6.0 | 44 | 3.7 | 113 | 18.6 | 15 | 44 | 3.7 | 39 |
| 1253A | 108 | 20.9 | 72 | 10.2 | 55 | 6.2 | 113 | 22.2 | 19 | 55 | 6.2 | 39 |
| 1503A | N/A | N/A | 86 | 16.0 | 66 | 9.5 | 113 | 25.5 | 23 | 66 | 9.5 | 39 |
| 1753A | N/A | N/A | 101 | 22.5 | 77 | 13.4 | 113 | 27.2 | 27 | 77 | 13.4 | 39 |
| 2003A | N/A | N/A | 115 | 31.9 | 88 | 18.9 | 115 | 30.2 | 31 | 88 | 18.9 | 39 |

* Closed systems only

Raypak, Inc. • Eastman Avenue, Oxnard, CA 93030 • (805) 278-5300 • (805) 872-9725 • www.raypak.com