# Hi Delta FlexGas - Type H

## Dual-Fuel Hot Water Boilers 
Models 992CD-2342CD

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

- 100% Factory Fire Tested

- Thermal Efficiency: 84%

- Versa IC® Controller with LCD Display

- Maximum Setpoint: 220°F

- Maximum Outlet Temperature: 240°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal Shock Proof Heat Exchanger

- Limited Twenty-Year Thermal Shock Warranty

- Limited Ten-Year Closed Loop Heat Exchanger Warranty

- Full Safety Diagnostics with Fault History

- PolyTuf Powder Coated Cabinet

Patent Nos. 6,904,873 & 7,044,124; other patents pending

No Combustible Floor Shield Required

- Fan-Assisted

Proudly Assembled in the USA

Patented Burner Security Blanket

- Ultra-Low NOx – SCAQMD 1146.2 Certified

- Cascade up to 4 Heaters – No External Sequencer Required

#### Heat Exchanger

Headers

Glass-Lined Cast Iron – Standard

A-1 Bronze

ASME Inspected and H-Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper – Standard

A-3 Cupro-Nickel

ASME Steel Tube Sheet

Silicone High Temp. O-Rings

ASME Pressure Relief Valve

60 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

A-6 Right

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

Versa IC® Integrated Control

100% Shut-Off/Lockout

Hot Surface Ignition

Ignition Module

- 3-Try – Standard

- C-6 Single Try

Remote Flame Sensor

Fixed High Limit, Manual Reset 240°F

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Programmable Pump Time Delays

Heater

Recirculation

- Enable/Disable

LCD Display; Status, Fault and Diagnostics

Cold Water Protection Function

- CWR Variable-Speed Pump

- (See Cat. 5000.73)

Modbus RTU BMS Port (Up to 115K Baud,

- B-85 – BMS Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

B-86 – BMS Gateway – LonWorks

#### Gas Train

Manual Gas Shut-Off Valve(s)

Gas Pressure Regulator

Safety Shut-Off Valve

Firing Control Valve

Firing Mode

3-Stage: Model 992CD (H8)

4-Stage: Model 1262CD-2342CD (H9)

Fuel

Natural Gas

Propane Gas (HD-5) (Excludes 2002CD)

G – 20 4” WC Nat Supply

Design Certified - ANSI Z21.13/CSA 4.9

#### Construction

Indoor/Outdoor Construction

Front Controls Enclosed

PolyTuf Powder Coat Finish

CSA Low Lead Certified ≤ .25% Lead

#### Venting

Vent Location

Top – Standard

D-14 Rear

Vent Termination Cap

D-11 Outdoor

D-15 Indoor, Horizontal

Indoor, Vertical (by others)

Combustion Air

D-17 In-Line Filter Kit (TruSeal 
only)

D-16 Air Intake Elbow

Extractor – Optional

By others

#### Not required

#### Burner

Ultra-Low NOx: Less than 20 PPM (NAT)

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Start (See 2000.48)

P-  	Cold Water Run (See 2000.48)

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack® Kit

X-2	SureRack Add-on

For Metric information, see Catalog

#### Additional Options or Accessories

For Metric information, see Catalog

#### Multi-Boiler Temperature Controllers

TempTracker Mod+ Hybrid

B-36, 2-4 Heaters

B-37, 5-10 Heaters

B-38, 11-16 Heaters

B-39 EMS 4-20mA Remote Setpoint Interface Module

B-62 BACnet MS/TP Interface

#### Hi Delta FlexGas – Type H

Models 992CD-2342CD	Model

RATES OF FLOW AND PRESSURE DROPS

NOTE:  Pump location varies based on model and application

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

| Model | 20ºF ΔT |  | 30ºF ΔT |  | Min. Flow |  |  | Max. Flow |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | GPM | ΔP (FT) | GPM | ΔP (FT) | GPM | ΔP (FT) | ΔT | GPM | ΔP (FT) | ΔT |
| 992CD | 84 | 5.6 | 56 | 2.5 | 42 | 1.5 | 40 | 132 | 14.0 | 13 |
| 1532CD | 107 | 10.0 | 71 | 4.5 | 53 | 2.6 | 40 | 132 | 15.5 | 16 |
| 1802CD | 130 | 16.0 | 86 | 7.1 | 65 | 4.1 | 40 | 132 | 16.5 | 20 |
| 2072CD | N/A | N/A | 117 | 15.0 | 88 | 8.7 | 40 | 132 | 19.5 | 27 |
| 2342CD | N/A | N/A | 132 | 21.0 | 99 | 12.0 | 40 | 132 | 21.0 | 30 |

Basis is 30 GPM or 40ºF ΔT for minimum flow, 132 GPM for maximum flow.

NOTES:

1.	Dimensions are in inches.

2.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

3.	Required natural gas supply pressure is 
7 - 10.5” WC. Required propane gas supply pressure is 11 - 13” WC.

| Model | MBTUH |  | Firing Stages | A Width | B | K | T | W | Amp Draw* | Approx. Shipping Wt. (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output |  |  |  |  |  |  |  |  |
| 992CD | 990 | 832 | 3 | 57-1/8 | 41-3/8 | 10 | 10 | 16-3/16 | <12 | 930 |
| 1262CD | 1260 | 1058 | 4 | 68-1/2 | 41-1/2 | 12 | 10 | 20-9/16 | <12 | 1040 |
| 1532CD | 1530 | 1285 | 4 | 79-7/8 | 36 | 12 | 10 | 24-3/8 | <12 | 1255 |
| 1802CD | 1800 | 1512 | 4 | 91-1/8 | 33-1/2 | 14 | 10 | 28-1/8 | <12 | 1380 |
| 2072CD | 2070 | 1739 | 4 | 102-1/2 | 39 | 14 | 10 | 31-15/16 | <12 | 1480 |
| 2342CD | 2340 | 1966 | 4 | 113-7/8 | 34 | 16 | 10 | 35-11/16 | <12 | 1550 |

*Without Pump