Job:

# Condensing Heat Exchanger (CHX)

## For use with the ADB™

Metric Data

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:

Exclusively for use with Raypak’s

ADVANCED DESIGN BOILER™ (ADB)

Boosts ADB efficiency to 97%!

The Raypak Condensing Heat Exchanger utilizes exhaust heat, which is normally wasted, and converts it to useful energy that increases overall operating efficiency.

Applications

- Hydronic Space Heating

- Hot Water Supply

Pool Heating

Advanced Design Boiler with CHX

FEATURES

- Finned cupro nickel tubes

- Patented epoxy coating

- All bronze headers

- AL29-4C stainless steel tube bundle casing

- Polytuf  powder coating on outer shell

- AL29-4C Stainless Steel vent adapter between the CHX and Advanced Design Boiler included

- ASME tested to 10.3 Bars working pressure

- Traditional Raypak tube sheet design with high-temperature silicone O-rings

- Condensate drain connection

- Indoor/outdoor construction

- Limited 20 year thermal shock warranty

- Footprint: less than .45 m2

- Ten year limited warranty

- National Board approved

For non-metric information,

see Catalog No.:  1000.90

#### Condensing Heat Exchanger (CHX)

Metric Data	Model

| MODEL | FITS ADB UNIT | A WIDTH | B* HEIGHT | F* | P* | U* | M* | T** | K | H** | X MIN. | Y | Z | SHIP WT. (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CHX 500 | ADB 500 | 59 | 63 | 48 | 28 | 56 | 35 | ½ | 15.2 | 2 | 71 | 21 | 9 | 113 |
| CHX 750 | ADB 750 | 59 | 78 | 61 | 38 | 70 | 42 | ½ | 20.3 | 2 | 71 | 25 | 8 | 125 |
| CHX 1000 | ADB 1000 | 73 | 99 | 84 | 55 | 93 | 52 | ½ | 25.4 | 2 ½ | 86 | 28 | 18 | 136 |

- 0.00

+2.54

Dimensions are in Centimeters (2.54 cm = 1 inch)	* Heights vary by 	 centimeters, using adjustable feet

** Gas and water connections are in NPT inches

ADB / ADB WITH CHX RATE OF FLOW AND PRESSURE DROP

|  | 11C T |  | 17C T |  | 22C T |  | MAX FLOW |  |  | MIN FLOW |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MODEL | LPM | P | LPM | P | LPM | P | LPM | P | T | LPM | P | T |
| ADB 500 W/ CHX | 159 185 | 7.8 13.5 | X 121 | X 6.9 | X X | X X | 318 318 | 26.3 33.8 | 6C 7C | 114 114 | 4.8 6.3 | 16C 18C |
| ADB 750 W/ CHX | 238 276 | 17.3 29.9 | 159 185 | 8.7 15.5 | X 136 | X 10.5 | 416 416 | 50.8 66.1 | 6C 7C | 121 121 | 5.4 7.2 | 22C 25C |
| ADB 1000 W/ CHX | 318 367 | 35.3 46.6 | 212 246 | 16.7 30.8 | 159 185 | 10.2 18.5 | 416 416 | 59.8 77.7 | 8C 10C | 159 159 | 10.2 13.5 | 22C 26C |

CHX RATE OF FLOW AND PRESSURE DROP

| MODEL | LPM | 114 | 125 | 159 | 197 | 318 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 500 | P | 1.5 | 1.8 | 2.7 | 3.3 | 7.5 |  |  |
| MODEL | LPM | 121 | 140 | 159 | 189 | 238 | 291 | 416 |
| 750 | P | 1.8 | 3.6 | 3.9 | 4.2 | 5.4 | 7.5 | 15.3 |
| MODEL | LPM | 159 | 193 | 212 | 250 | 318 | 367 | 416 |
| 1000 | P | 3.3 | 4.8 | 5.4 | 8.4 | 13.2 | 15.2 | 17.9 |

Raypak, Inc.  31111 Agoura Road, Westlake Village, CA 91361-4699  (818) 889-1500  Fax (818) 889-4522  www.raypak.com

Raypak Canada LTD.  2805 Slough Street, Mississauga, Ontario, Canada L4T 1G2  (905) 677-7999  Fax: (905) 677-8036  www.raypakcanada.com

Raypak Australia Pty. Ltd  7 Geddes Street, Mulgrave, Victoria, Australia 3170  (6139) 560 4944  Fax (6139) 560 4974   www.raypak.com.au