Job:

# B-60 Stage Interface
Up to 4-Stage Controller

# For Hi Delta® and Raytherm® Boilers & Water Heaters

Engineer:

Contractor:

Prepared By:

Date:

B-60 Stage Interface is designed to stage a single boiler of up to four total stages using a proportional DC voltage or milliamp current signal from a building management system or multi-boiler controller such as our TempTracker MOD+ Hybrid. It is available factory-mounted on Hi Delta and Raytherm stage fired boilers as well as available as a field install kit.

#### Features

- Four stages of relay control

- Voltage or current input

- 24 VAC/VDC power

- LED indication of relay status

- Adjustable relay setpoints

- Adjustable relay differentials

Snap-track mounted

SPECIFICATIONS:

Supply Voltage		24VAC±10%@160mA

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

24VDC±10%@80mA

Input Signal	0-20mA or 0-10VDC

(15VDC Max)

jumper selectable

Output	Four SPDT relays

Relay Rating	10A@120VAC

Input Impedance	250Ω (mA input)

49.7 KΩ (VAC input)

Operating Temp	32° to 158°F (0° to 70°C)

Humidity Limit	5% to 95% RH non-condensing

Relay Differential	.5mA or .375V

Model Information

Factory Mounted

Field Install Kit

| Relay | Relay Pull-In Voltage | Relay Pull-In Current | 2 Stage | 3 Stage | 4 Stage |
| --- | --- | --- | --- | --- | --- |
| 1 | 0.75 VDC | 1.5 mA |  |  |  |
| 2 | 3.0 VDC | 6.1 mA |  |  |  |
| 3 | 5.5 VDC | 11.12 mA |  |  |  |
| 4 | 8.0 VDC | 16.23 mA |  |  |  |