# Hi Delta SS®- Type H

## Space Heating/Hot Water Boiler Models HD101-HD401

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

TruSeal® Direct Vent

Sealed Combustion Chamber

100% Factory Fire Tested

Efficiency: HD101 – HD 301 85% AFUE

HD401 -              84% Thermal

Maximum Outlet Temperature: 240°F

Minimum Non-condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-year Thermal Shock Warranty

Limited Ten-year Closed-System Heat Exchanger Warranty

Status Display LED’s

PolyTuf Powder-Coated Cabinet

Proudly Assembled in the USA

No Combustible Floor Shield Required

Fan-assisted – Ultra Low NOx (<20 ppm Nat.)

Patented Burner Security Blanket

#### Heat Exchanger

H Stamp

Headers

Cast Iron, Glass-lined – Standard

A-1 Bronze

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Finned Tubing

Copper – Standard

A-3 Cupro-Nickel

ASME Steel Tube Sheet

Silicone High-Temp O-Rings

Pressure Relief Valve - ASME

45 PSIG - Standard

PSIG - Optional

Temperature and Pressure Gauge (shipped loose)

Flow Switch - Mounted

Left-hand Water (Standard)

A-6 Right-hand water

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

100% Shutoff/Lockout

Hot Surface Ignition

Remote Flame Sensor

Fixed High Limit Control, Manual Reset

On/Off Power Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switches (2)

Economaster Style Pump Relay

Electronic Outdoor Reset Controller (HD101 – HD301 Only) 2-Stage Controller w/Outdoor Reset, Setpoint 120-200°F

#### Gas Train

4” WC Minimum Pressure

Combination Valve

Firing Mode

Two-stage (H3) - Standard

On/Off (H4) - Optional

Fuel

Natural Gas

Propane Gas

Design Certified
ANSI Z21.13/CSA 4.9

#### Burner

Two-stage

Ultra-low NOx (<20 ppm Nat.)

#### Construction

Indoor/Outdoor Construction

Slide-out Controls Tray

Front Controls Enclosed

PolyTuf Powder Coat Finish

TruSeal® Direct Vent

Integral Combustion Air Filter

#### Venting

Vent Termination Cap

D-11 Outdoor

D-15 Indoor, Horizontal

D-20 Indoor, Vertical

Combustion Air - Ducted

D-16 Air Intake Elbow

Extractor – Optional

By others

Not required

#### Temperature Controls (HD-401 Only)

B-3	1-Stage Controller, 100-200°F (Loose)

B-6	2-Stage Controller, 130-230°F (Loose)

B-21	TempTracker Digital Controller 4-Stage (loose)

B-26	TempTracker Digital Controller, 2-Stage (Mtd)

B-27 	TempTracker Digital Controller, 2-Stage, O/D (Mtd)

B-28	On/Off Digital Controller, (Mtd)

B-42	Electronic Controller, 2-stg, Outdoor Reset, 120° - 200°F (Mtd)

B-32	 Remote Controller

By others:

#### Options

F-10	Low Water Cut-off, Remote Probe

I-1	Adjustable High Limit Control, Auto Reset

P-  	Pump:      HP, 120V, 160 Hz
 Bronze	 Mounted

Cast Iron	 Loose

P-  	Cold Water Protection (See 1000.19)

S-__ Low and High Gas Pressure Switches, Manual

#### Hi Delta SS HD101-HD401

#### Type H - Hydronic Heating	Model

| Model H3- |  |
| --- | --- |
| HD101 | 0010 1/8 – 1.3 |
| HD151 |  |
| HD201 |  |
| HD251 |  |
| HD301 |  |
| HD401 |  |

Primary Pump HP - Amps

|  |  |  |  |  |  |  |  |  | APPROX. SHIP WT. (LBS.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MODEL | MBTUH |  | AFUE (%) | A | B | K | Z | Boiler Amps‡ |  |
|  | INPUT | OUTPUT |  |  |  |  |  |  |  |
| HD101 | 100 | 84 | 85 | 18-9/16 | 9-1/4 | 4 | 19-15/16 | <5 | 150 |
| HD151 | 150 | 126 |  | 21-7/8 | 10-7/8 | 4 | 23-3/16 | <5 | 175 |
| HD201 | 199 | 167 |  | 25-1/16 | 12-1/2 | 5 | 26-7/16 | <5 | 200 |
| HD251 | 250 | 210 |  | 28-5/16 | 14-1/8 | 5 | 29-11/16 | <5 | 225 |
| HD301 | 299 | 251 |  | 31-9/16 | 15-3/4 | 5 | 32-15/16 | <5 | 250 |
| HD401 | 399 | 335 | 84* | 38-1/16 | 19 | 6 | 39-7/16 | <5 | 300 |

Dimensions are in inches.

‡ Amp draw does not include pump.	* Thermal Efficiency

RATES OF FLOW AND PRESSURE DROPS

| MODEL | Input MBTUH | Output MBTUH | 10ºF ∆T |  | 20ºF ∆T |  | 30ºF ∆T |  | MIN. FLOW |  |  | MAX. FLOW |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) | ∆T | GPM | ∆P (ft) | ∆T |
| HD101 | 100 | 84 | 17 | 1.2 | N/A | N/A | N/A | N/A | 13 | 0.8 | 13 | 44 | 8.8 | 4 |
| HD151 | 150 | 126 | 25 | 2.9 | 13 | 0.8 | N/A | N/A | 13 | 0.8 | 20 | 44 | 8.8 | 6 |
| HD201 | 199 | 167 | 33 | 5.2 | 17 | 1.3 | N/A | N/A | 13 | 3.3 | 27 | 44 | 8.9 | 8 |
| HD251 | 250 | 210 | 44 | 9.2 | 21 | 2.1 | 14 | 0.9 | 13 | 0.7 | 34 | 44 | 9.2 | 10 |
| HD301 | 299 | 251 | N/A | N/A | 25 | 3.1 | 17 | 1.3 | 13 | 0.7 | 40 | 44 | 9.4 | 11 |
| HD401 | 399 | 335 | N/A | N/A | 34 | 5.6 | 22 | 2.5 | 22 | 2.5 | 30 | 44 | 9.8 | 15 |

NOTE: Basis for minimum flow is 13 GPM or 40°F ∆T.

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 2,000 feet. For installations above 2,000 feet, please contact manufacturer.

2.	Recommended natural gas pressure is 7 – 10.5” WC. Recommended propane gas pressure is 11 - 13” WC.

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com