# MVB® - Type WH

## Water Heaters
Models 504A-2004A

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- 83% to 83.3% Thermal Efficiency at full rate

- 100% Factory Fire-Tested

- VERSA IC® Integrated Controller with 7” color touchscreen display

- Raymote™ remote connectivity provided standard

- On/Off Firing with Soft-Start ignition

- Full Safety Diagnostics with History

- Status Display Lights

- Cascade up to 4 Heaters – No External Sequencer Needed

- Modbus RTU BMS Port

- CSA Low Lead Certified ≤.25% Lead

- Maximum Outlet Water Temperature: 200°F

- Maximum Tank Setpoint: 150°F

- Minimum Acceptable Inlet Water Temperature: 120°F

Proudly Assembled in the USA

Limited Five-Year Copper/Ten-Year Cupronickel Heat Exch. Warranty

- Ultra-Low NOx, Less than 20 PPM

#### Heat Exchanger

- Headers - Bronze

- ASME HLW Stamped
160 PSIG MAWP

- National Board Approved

- Fin Tubing

Copper – Standard

A-3 Cupronickel

- ASME Powder-Coated Tube Sheet

- Silicone High-Temp O-Rings

- ASME Pressure Relief Valve

125 PSIG – Standard

150 PSIG – Optional

- Temperature and Pressure Gauge,
Shipped Loose

- Four pass primary heat exchanger

- Stainless Steel Evaporator Plate

#### Control

- 120V, 60Hz, 1Ø, Power Supply

- 120/24V 60Hz Transformer

- VERSA IC® built-in controller

- 7” color HD touchscreen display

- Raymote Wi-Fi remote connectivity

- Cascade up to 4 Heaters

- Ignition Module

3-Try – Standard

C-6 Single-Try

- Remote Flame Sensor

- Freeze Protection

- High Limit, Manual Reset, Fixed, 200ºF

- On/Off Power Switch

- Flow Switch

- Blocked Vent Pressure Switch

- Programmable Pump Time Delays

- Pump Outputs

- Water Heater

- System – Pilot Duty

#### Control (cont.)

- Water Temperature Sensors (3)

- Cold Water Protection Function

- Optional Variable-Speed Pump

- Modbus RTU BMS Port

B-85   BMS Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

B-86   BMS Gateway – LonWorks

#### Burner

- Hot Surface Ignition (HSI)

- Radially-Fired Knitted Burner

#### Gas Train

- Fuel

Natural Gas

Propane (Minimum Grade HD-5)

- Dual-Seat Combination Firing Valve

- Manual Shut-Off Valve

#### Construction

- Indoor/Outdoor Construction

- Front Controls Enclosed

- PolyTuf Powder Coat Finish

- Rear Connections (Water, Electrical, Gas, Vent, Combustion Air)

- In-line Combustion Air Filter Kit

- Design Certified ANSI Z21.10.3/CSA 4.3

- CSA Low Lead Certified ≤.25% Lead

#### Venting

Vent Termination

D-11 Outdoor

D-15 Indoor, Horizontal

Indoor, Vertical (by others)

Combustion Air

D-16 Air Intake Elbow

Extractor – Optional

By others

Not required

#### Options

A-30	Air Vent, Auto, 150 PSI (loose)

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit, Auto Reset, Adj., 
40-180F

I-2	High Limit, Manual Reset, Adj., 100-200F (additional)

P-  	Pump:      HP, 120V, 1, 60Hz

Water Hardness:         GPG

Bronze

Loose	 Mounted

P-  	Cold Water Run

S-1	Low Gas Pressure Switch, 
Manual Reset

S-2	High Gas Pressure Switch, Manual Reset

Z-12	Condensate Treatment Kit

#### Additional Options or Accessories

MVB – Type WH

Models 504A-2004A	Model

| Model (WH1-) | MBTUH |  |  | Dimensions (in.) |  |  |  |  |  |  |  |  |  |  |  | Ship Weight (Lbs.) | Foot- print (Ft2) | Amps** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | B | D | E | F | G* | H | K | L | M | N | P | R | V |  |  |  |
|  | Input | Output | Height |  |  |  | NPT | NPT | Flue Ø |  |  | C/A Ø |  |  |  |  |  |  |
| 504A | 500 | 415 | 43 | 30 | 35 | 23-3/4 | 1 | 2 | 8 | 13-3/4 | 14-1/8 | 6 | 36 | 8 | 2 | 600 | 5.4 | 12 |
| Raypak, Inc. 2151 Eastman Avenue, Oxnard, CA 93030 (805) 278-5300 Fax (800) 872-9725 www.raypak.com 754A | 750 | 623 | 49 | 36 | 41 | 29-3/4 | 1 | 2 | 10 | 13-1/2 | 16 | 6 | 42 | 8 | 2 | 670 | 5.4 | 12 |
| 1104A | 1045 | 870 | 55 | 43 | 47 | 35-3/4 | 1-1/4 | 2-1/2 | 10 | 13-1/2 | 16 | 6 | 49 | 8 | 2 | 720 | 5.4 | 12 |
| 1504A | 1425 | 1187 | 61 | 50 | 53 | 41-3/4 | 1-1/4 | 2-1/2 | 12 | 13-3/4 | 18-1/8 | 8 | 53 | 8 | 2 | 780 | 5.4 | 12 |
| 2004A | 1900 | 1583 | 75 | 61 | 65 | 53-3/4 | 2 | 2-1/2 | 14 | 13-1/2 | 20-1/8 | 8 | 69 | 9 | 5 | 940 | 5.4 | 18 |

| - Ratings shown are for elevations up to 4,500 feet. For installations at elevations above 4,500 feet, please consult the factory for additional instructions. NO hardware changes required under 10,000 ft. * For Natural Gas. For Propane, all Sizes 1 NPT. ** Current draw is for heater only. (Supply breaker must have delayed trip.) |  |
| --- | --- |

MVB – Type WH

Models 504A-2004A	Model

PUMP HP – AMPS*						CLEARANCES

| Model (WH-1) | Water Hardness |  |  |
| --- | --- | --- | --- |
|  | Soft | Medium | Hard |
| 504A | 1/4 – 6 | 1/4 – 6 | 3/4 - 11 |
| 754A | 1/4 – 6 | 1/2 – 7 | 3/4 - 11 |
| 1104A | 1/4 – 6 | 1/2 – 7 | 1 - 14 |
| 1504A | 1/2 – 7 | 1 - 14 | 1 - 14 |
| 2004A | 1 – 14 | 1 1/2 - 16 | 1 1/2 - 16 |

|  | Certified Minimum | Recommended Service |
| --- | --- | --- |
| Front | 24” | 24” |
| Rear | 12” | 24” |
| Right | 1” | 1” |
| Left | 1” | 1” |
| Top | 0” | 10” |
| Floor | 0” | 0” |
| Vent | 1” | 1” |

*Current draw is for pump only

SHL includes 50ft of tubing each way (total 100 ft.).

* Must use optional cupronickel heat exchanger.

** If over 25 GPG, a water softener MUST be used.

|  | Water Hardness |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Soft |  |  |  |  | Medium |  |  |  |  | Hard* |  |  |  |  |
|  | 3-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25 Grains Per Gallon** |  |  |  |  |
| Model | ΔT (ºF) | GPM | ΔP (ft wc) | MTS (in) | SHL (ft wc) | ΔT (ºF) | GPM | ΔP (ft wc) | MTS (in) | SHL (ft wc) | ΔT (ºF) | GPM | ΔP (ft wc) | MTS (in) | SHL (ft wc) |
| 504A | 17 | 50 | 3.6 | 2 | 8.3 | 17 | 50 | 3.6 | 2 | 8.3 | 9 | 95 | 10.4 | 2 | 25.7 |
| 754A | 25 | 50 | 4.0 | 2 | 8.7 | 17 | 73 | 7.8 | 2 | 17.3 | 14 | 90 | 11.4 | 2 | 25.3 |
| 1104A | 20 | 85 | 11.5 | 2-1/2 | 16.2 | 20 | 85 | 11.5 | 2-1/2 | 16.2 | 15 | 116 | 19.6 | 2-1/2 | 27.8 |
| 1504A | 25 | 94 | 18.4 | 2-1/2 | 24.0 | 23 | 105 | 22.5 | 2-1/2 | 29.3 | 21 | 115 | 26.5 | 2-1/2 | 34.6 |
| 2004A | 29 | 109 | 28.6 | 2-1/2 | 36.0 | 29 | 109 | 28.6 | 2-1/2 | 36.0 | 29 | 109 | 28.6 | 2-1/2 | 36.0 |

|  | Recovery Rates |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Temperature Rise (°F) |  |  |  |  |  |  |  |  |  |
|  | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 |
| 504A | 2515 | 1677 | 1258 | 1006 | 838 | 719 | 629 | 559 | 503 | 457 |
| 754A | 3773 | 2515 | 1886 | 1509 | 1258 | 1078 | 943 | 838 | 755 | 686 |
| 1104A | 5226 | 3517 | 2638 | 2110 | 1759 | 1507 | 1319 | 1172 | 1055 | 959 |
| 1504A | 7194 | 4796 | 3597 | 2878 | 2398 | 2055 | 1799 | 1599 | 1439 | 1308 |
| 2004A | 9592 | 6395 | 4796 | 3837 | 3197 | 2741 | 2398 | 2132 | 1918 | 1744 |

Raypak, Inc. ▪ 2151 Eastman Avenue, Oxnard, CA 93030 ▪ (805) 278-5300 ▪ Fax (805) 872-9725 ▪ www.raypak.com