# MVB® - Type WH

## Water Heaters
Models 503A-2003A

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- 87% Thermal Efficiency at Full Rate

- 100% Factory Fire-Tested

- VERSA IC® Modulating Controller with with 7” color touchscreen display

- Raymote™ remote connectivity provided standard

- On/Off Firing with Soft-Start Ignition

- Full Safety Diagnostics with History

- Status Display Lights

- Cascade up to 4 Heaters – No External Sequencer Required

- Modbus RTU BMS Port

- CSA Low Lead Certified ≤.25% Lead

- Maximum Outlet Water Temperature: 200°F

- Maximum Tank Setpoint: 150°F

Proudly Assembled in the USA

Minimum Acceptable Inlet Water Temperature: 120°F

- Limited Five-Year Copper/Ten-Year Cupro-Nickel Heat Exch. Warranty

- Ultra Low NOx, Less than 20 PPM

#### Heat Exchanger

- Headers, Bronze

- ASME HLW Stamped
160 PSIG MAWP

- National Board Approved

- Fin Tubing

Copper – Standard

A-3 Cupronickel

- ASME Powder-Coated Tube Sheet

- Silicone High-Temp O-Rings

- ASME Pressure Relief Valve

125 PSIG – Standard

150 PSIG – Optional

- Temperature and Pressure Gauge,
Shipped Loose

- Four pass primary heat exchanger

- Stainless Steel Evaporator Plate

#### Control

- 120V, 60Hz, 1Ø, Power Supply

- 120/24V 60Hz Transformer

- VERSA IC® built-in controller

- 7” color HD touchscreen display

- Raymote Wi-Fi remote connectivity

- Cascade up to 4 Heaters

- Ignition Module

3-Try – Standard

C-6 Single-Try

- Remote Flame Sensor

- Freeze Protection

- High Limit, Manual Reset, Fixed, 200ºF

- On/Off Power Switch

- Flow Switch

- Blocked Vent Pressure Switch

- Programmable Pump Time Delays

- Pump Outputs

- Water Heater

- System – Pilot Duty

- Modulating Temperature Control

- Water Temperature Sensors (3)

- Cold Water Protection Function

- Optional Variable-Speed Pump

- Modbus RTU BMS Port

- B-85    Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

- B-86    Gateway - LonWorks

#### Burner

- Radially-Fired Knitted Burner

- Hot Surface Ignition (HSI)

#### Gas Train

- Fuel

Natural Gas

Propane (Minimum Grade HD-5)

- Dual-Seat Combination Firing Valve

- Manual Shut Off Valve

#### Construction

- Indoor/Outdoor Construction

- Front Controls Enclosed

- PolyTuf Powder Coat Finish

- Rear Connections (Water, Electrical, Gas, Vent, Combustion Air)

- In-line Combustion Air Filter Kit

- Design Certified ANSI Z21.10.3/CSA 4.3

- CSA Low Lead Certified ≤.25% Lead

#### Venting

- Vent Termination

D-11 Outdoor

D-15 Indoor, Horizontal

Indoor, Vertical (by others)

- Combustion Air

D-16 Air Intake Elbow

- Extractor – Optional

By others

Not required

#### Options

A-30	Air Vent, Auto, 150 PSI (Loose)

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit, Auto Reset, Adj., 
40-180F

I-2	High Limit, Manual Reset, Adj., 100-200F (additional)

P-  	Bronze Pump:      HP, 120V, 1, 60Hz

Water Hardness:         GPG

Loose	 Mounted

P-  	Cold Water Run

S-1	Low Gas Pressure Switch, 
Manual Reset

S-2	High Gas Pressure Switch, Manual Reset

Z-12	Condensate Treatment Kit

#### Additional Options or Accessories

MVB® – Type WH

Models 503A-2003A	Model

|  | Certified Minimum | Recomm. Service |
| --- | --- | --- |
| Front | 24” | 24” |
| Rear | 12” | 24” |
| Right | 1’ | 1” |
| Left | 1” | 1” |
| Top | 0” | 10” |
| Floor | 0” | 0” |
| Vent | 1” | 1” |

Clearances

| Model (WH1-) | MBTUH |  |  | Dimensions (in.) |  |  |  |  |  |  |  |  |  |  |  | Ship Weight (Lbs.) | Foot- print (Ft2) | Amps** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | B | D | E | F | G* | H | K | L | M | N | P | R | V |  |  |  |
|  | Input | Output | Height |  |  |  | NPT | NPT | Flue Ø |  |  | C/A Ø |  |  |  |  |  |  |
| 503A | 500 | 435 | 43 | 32 | 35 | 23-3/4 | 1 | 2 | 6 | 13-3/4 | 14-1/4 | 6 | 35 | 8 | 2 | 600 | 5.4 | 12 |
| 753A | 750 | 653 | 49 | 38 | 41 | 29-3/4 | 1 | 2 | 6 | 13-1/2 | 14-1/4 | 6 | 41 | 8 | 2 | 670 | 5.4 | 12 |
| 1003A | 999 | 869 | 55 | 44 | 47 | 35-3/4 | 1-1/4 | 2-1/2 | 6 | 13-1/2 | 14-1/4 | 6 | 47 | 8 | 2 | 720 | 5.4 | 12 |
| 1253A | 1250 | 1088 | 61 | 50 | 53 | 41-3/4 | 1-1/4 | 2-1/2 | 8 | 13-3/4 | 17-1/4 | 8 | 53 | 8 | 2 | 780 | 5.4 | 12 |
| 1503A | 1500 | 1305 | 67 | 56 | 59 | 47-3/4 | 1-1/4 | 2-1/2 | 8 | 13-3/4 | 17-1/4 | 8 | 59 | 8 | 2 | 840 | 5.4 | 12 |
| 1753A | 1750 | 1523 | 75 | 62 | 65 | 53-3/4 | 2 | 2-1/2 | 8 | 13-1/2 | 17-1/4 | 8 | 68 | 9 | 5 | 940 | 5.4 | 18 |
| 2003A | 1999 | 1739 | 81 | 68 | 71 | 59-3/4 | 2 | 2-1/2 | 8 | 13-3/4 | 17-1/4 | 8 | 74 | 9 | 5 | 1000 | 5.4 | 18 |

| *For natural gas. For propane, all sizes are 1” NPT **Current draw is for heater only. (Supply breaker must have delayed trip.) - Ratings shown are for elevations up to 4,500 feet. For installations at elevations above 4,500 feet, please consult the factory for additional instructions. No hardware changes required below 10,000 feet. |  |
| --- | --- |

MVB® – Type WH

Models 503A-2003A	Model

PUMP HP – AMPS*

| Model (WH-1) | Water Hardness |  |  |
| --- | --- | --- | --- |
|  | Soft | Medium | Hard |
| 503A | 1/4 – 6 | 1/4 – 6 | 3/4 – 11 |
| 753A | 1/4 – 6 | 1/2 – 7 | 3/4 – 11 |
| 1003A | 1/4 – 6 | 1/2 – 7 | 1 – 14 |
| 1253A | 1/2 – 7 | 1 – 14 | 1 – 14 |
| 1503A | 3/4 – 11 | 1 – 14 | 1 – 14 |
| 1753A | 1 – 14 | 1 1/2 – 16 | 1 1/2 – 16 |
| 2003A | 1 – 14 | 1 1/2 – 16 | 1 1/2 – 16 |

* Current draw is for pump only.

SHL includes 50ft of tubing each way (total 100 ft)

* Must use optional cupronickel heat exchanger

** If over 25 GPG, a water softener MUST be used.

|  | Water Hardness |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Soft |  |  |  |  | Medium |  |  |  |  | Hard* |  |  |  |  |
|  | 3-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25 Grains Per Gallon** |  |  |  |  |
| Model | ΔT (ºF) | GPM | ΔP (ft wc) | MTS (in) | SHL (ft wc) | ΔT (ºF) | GPM | ΔP (ft wc) | MTS (in) | SHL (ft wc) | ΔT (ºF) | GPM | ΔP (ft wc) | MTS (in) | SHL (ft wc) |
| 503A | 17 | 50 | 3.6 | 2 | 8.3 | 17 | 50 | 3.6 | 2 | 8.3 | 9 | 95 | 10.4 | 2 | 25.7 |
| 753A | 26 | 50 | 4.0 | 2 | 8.7 | 18 | 73 | 7.8 | 2 | 17.3 | 15 | 90 | 11.4 | 2 | 25.3 |
| 1003A | 20 | 85 | 11.5 | 2-1/2 | 16.2 | 20 | 85 | 11.5 | 2-1/2 | 16.2 | 15 | 116 | 19.6 | 2-1/2 | 27.8 |
| 1253A | 27 | 80 | 12.2 | 2-1/2 | 16.3 | 20 | 109 | 21.0 | 2-1/2 | 28.3 | 20 | 109 | 21.0 | 2-1/2 | 28.3 |
| 1503A | 28 | 94 | 18.4 | 2-1/2 | 24.0 | 25 | 105 | 22.5 | 2-1/2 | 29.3 | 23 | 115 | 26.5 | 2-1/2 | 34.6 |
| 1753A | 29 | 104 | 23.6 | 2-1/2 | 30.3 | 27 | 113 | 27.4 | 2-1/2 | 35.2 | 27 | 113 | 27.4 | 2-1/2 | 35.2 |
| 2003A | 32 | 108 | 28.1 | 2-1/2 | 35.3 | 32 | 108 | 28.1 | 2-1/2 | 35.3 | 30 | 116 | 33.0 | 2-1/2 | 41.5 |

|  | RECOVERY RATES |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Temperature Rise (°F) |  |  |  |  |  |  |  |  |  |
|  | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 |
| 503A | 2636 | 1758 | 1318 | 1055 | 879 | 753 | 659 | 586 | 527 | 479 |
| 753A | 3955 | 2636 | 1977 | 1582 | 1318 | 1130 | 989 | 879 | 791 | 719 |
| 1003A | 5267 | 3512 | 2634 | 2107 | 1756 | 1505 | 1317 | 1171 | 1053 | 958 |
| 1253A | 6591 | 4394 | 3295 | 2636 | 2197 | 1883 | 1648 | 1465 | 1318 | 1198 |
| 1503A | 7909 | 5273 | 3955 | 3164 | 2637 | 2260 | 1978 | 1758 | 1582 | 1438 |
| 1753A | 9227 | 6152 | 4614 | 3691 | 3076 | 2636 | 2307 | 2051 | 1845 | 1678 |
| 2003A | 10540 | 7027 | 5270 | 4216 | 3513 | 3011 | 2635 | 2342 | 2108 | 1916 |

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com