# Hi Delta - Type H

## Space Heating/Hot Water Boilers Models 302C-902C

# Hi Delta - Type H

## Space Heating/Hot Water Boilers Models 302C-902C

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

- 100% Factory Fire Tested

- Thermal Efficiency: 84%

- Versa IC® Controller with LCD Display

- Maximum Setpoint: 220°F

- Maximum Outlet Temperature: 230°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal Shock Proof Heat Exchanger

- Limited Twenty-Year Thermal Shock Warranty

- Limited Ten-Year Closed-System Heat Exchanger Warranty

- Cascade up to 4 Heaters – No External Sequencer Required

- Full Safety Diagnostics with Fault History

Proudly Assembled in the USA

Proudly Assembled in the USA

PolyTuf Powder Coated Cabinet

- No Combustible Floor Shield Required

- Fan-Assisted

- Patented Burner Security Blanket

- Ultra-Low NOx – SCAQMD 1146.2 Certified

#### Heat Exchanger

Headers

Glass-Lined Cast Iron – Standard

A-1 Brass

ASME Inspected and H Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper – Standard

A-3 Cupro-Nickel

ASME Steel Tube Sheet

Silicone High-Temp. O-Rings

ASME Pressure Relief Valve

45 PSIG – Standard on Models 302C and 402C

60 PSIG – Standard on Models 502C-902C

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

A-6 Right Hand

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

Versa IC® Integrated Control

100% Shut-Off/Lockout

Hot Surface Ignition

Ignition Module

- 3-Try – Standard

- C-6 Single Try

Remote Flame Sensor

Fixed High Limit, Manual Reset 240°F

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Programmable Pump Time Delays

Boiler

Indirect Storage Tank

System

Enable/Disable

LCD Display; Status, Fault and Diagnostics

Cold Water Protection Function

- CWS Three-Way Valve

- CWR Variable-Speed Pump

Modbus RTU BMS Port (Up to 115K Baud, See Cat. 5000.73)

- B-85 – BMS Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

- B-86 – BMS Gateway - LonWorks

#### Gas Train

Manual Gas Shut-Off Valve(s)

Combo Valve(s)

Firing Mode

2-Stage (H3): Models 302B-902B

Fuel

Natural Gas

Propane Gas (HD-5)

G – 20 4” WC Nat Supply

Design Certified ANSI Z21.13/CSA 4.9

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

CSA Low Lead Certified (≤ .25% Lead)

#### Venting

Vent Location

Top – Standard

D-14 Rear

Vent Termination Cap

D-11 Outdoor

D-15 Indoor, Horizontal

Indoor, Vertical (by others)

Combustion Air

D-17 In-Line Filter Kit (TruSeal only)

D-16 Air Intake Elbow

Extractor – Optional

By others

Not required

#### Options

D-21	TruSeal Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 1, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack® Kit

X-2	SureRack Add-on

For Metric information, see Catalog

For Metric information, see Catalog

#### Additional Options or Accessories

For Metric information, see Catalog

For Metric information, see Catalog

#### Multi-Boiler Temperature Controllers

TempTracker Mod+ Hybrid

B-36, 2-4 Heaters

B-37, 5-10 Heaters

B-38, 11-16 Heaters

B-39 EMS 4-20mA Remote Setpoint Interface Module

B-62 BACnet MS/TP Interface

#### Hi Delta – Type H

#### Models 302C-902C 	Model

NOTE: Pump location varies based on model and application

NOTE: Pump location varies based on model and application

| SPECIFICATIONS |  |  |  |  |  |  |  |  | Approx. Shipping Wt. (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | MBTUH |  | A Width | G NPT | H NPT | K | W | Amp. Draw |  |
|  | Input | Output |  |  |  |  |  |  |  |
| 302C | 300 | 252 | 36 | 3/4 | 2 | 6 | 14-3/4 | 6 | 380 |
| 402C | 399 | 335 | 43 | 3/4 | 2 | 6 | 18-1/2 | 6 | 445 |
| 502C | 500 | 420 | 50 | 1-1/4 | 2 | 6 | 22 | 6 | 545 |
| 652C | 650 | 546 | 60-1/2 | 1-1/4 | 2 | 8 | 27-1/4 | 6 | 590 |
| 752C | 750 | 630 | 67-1/2 | 1-1/4 | 2 | 8 | 30-3/4 | 6 | 675 |
| 902C | 900 | 756 | 78 | 1-1/4 | 2 | 8 | 36 | 7 | 740 |

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

2.	Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

2.	Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.

Dimensions are in inches.

Dimensions are in inches.

| RATES OF FLOW AND PRESSURE DROPS |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | 10°F ΔT |  | 20°F ΔT |  | 30°F ΔT |  | Min. Flow |  |  | Max. Flow |  |  |
|  | GPM | ΔP (ft.) | GPM | ΔP (ft.) | GPM | ΔP (ft.) | GPM | ΔP (ft.) | ΔT | GPM | ΔP (ft.) | ΔT |
| 302C | 51 | 3.2 | 25 | <1.0 | N/A | N/A | 20 | <1.0 | 25 | 90 | 9.8 | 6 |
| 402C | 68 | 5.4 | 34 | 1.5 | 22 | <1.0 | 20 | <1.0 | 34 | 90 | 10.0 | 7 |
| 502C | 85 | 9.2 | 42 | 2.3 | 28 | 1.1 | 21 | <1.0 | 39 | 90 | 10.5 | 9 |
| 652C | N/A | N/A | 55 | 4.0 | 36 | 1.8 | 28 | 1.1 | 39 | 90 | 10.7 | 12 |
| 752C | N/A | N/A | 64 | 5.5 | 42 | 2.5 | 32 | 1.6 | 39 | 90 | 11.0 | 14 |
| 902C | N/A | N/A | 76 | 8.5 | 51 | 3.8 | 38 | 2.2 | 39 | 90 | 11.8 | 17 |

NOTES:

NOTES:

- Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installations above 4,500 feet, please contact manufacturer.

- Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 – 13” WC.

- Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installations above 4,500 feet, please contact manufacturer.

- Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 – 13” WC.

Basis is 20 GPM or 39°F ΔT for minimum flow, 90 GPM for maximum flow

Basis is 20 GPM or 39°F ΔT for minimum flow, 90 GPM for maximum flow

RATES OF FLOW AND PRESSURE DROPS

|  | 10°F ∆T |  | 20°F ∆T |  | 30°F ∆T |  | ###### Min. Flow |  |  | ###### Max. Flow |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### Model | ###### GPM | ∆P (ft) | ###### GPM | ∆P (ft) | ###### GPM | ∆P (ft) | ###### GPM | ∆P (ft) | ###### ∆T | ###### GPM | ∆P (ft) | ###### ∆T |
| 302C | 51 | 3.2 | 25 | <1.0 | N/A | N/A | 20 | <1 | 25 | 90 | 9.8 | 6 |
| 402C | 68 | 5.4 | 34 | 1.5 | 22 | <1 | 20 | <1 | 34 | 90 | 10.0 | 7 |
| 502C | 85 | 9.2 | 42 | 2.3 | 28 | 1.1 | 21 | <1 | 39 | 90 | 10.5 | 9 |
| 652C | N/A | N/A | 55 | 4.0 | 36 | 1.8 | 28 | 1.1 | 39 | 90 | 10.7 | 12 |
| 752C | N/A | N/A | 64 | 5.5 | 42 | 2.5 | 32 | 1.6 | 39 | 90 | 11.0 | 14 |
| 902C | N/A | N/A | 76 | 8.5 | 51 | 3.8 | 38 | 2.2 | 39 | 90 | 11.8 | 17 |

Basis is 20 GPM or 39°F ∆T for minimum flow, 90 GPM for maximum flow.