Job:

# Delta Limited™ - Type H

## Space Heating/Hot Water Boiler Models 989B-2339B

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

100% Factory Fire Tested

Efficiency: 84%

Maximum Outlet Temperature: 230°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Year Thermal Shock Warranty

Limited Ten-Year Closed-System Heat Exchanger 
Warranty

Shown with outdoor 
air inlet and pump covers

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-Assisted

Proudly Assembled in the USA

Patented Burner Security Blanket

- Heat Exchanger

- H Stamp

- Headers

Glass-Lined Cast Iron – Standard

Bronze – Option A-1

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

- ASME Steel Tube Sheet

- Silicone High Temp O-Rings

- ASME Pressure Relief Valve

60 PSIG – Standard

PSIG – Optional

- Temperature and Pressure Gauge

- Water Connections

Left – Standard

Right – Option A-6

#### Controls

- 120V, 60Hz, 1 Phase Power 
Supply

- 120/24V 60Hz Transformer

- 100% Shut-Off/Lockout

- Hot Surface Ignition

- Remote Flame Sensor

- High Limit Control, Manual Reset

- On/Off Power Switch

- Manual Shut-Off, Front-Mounted Switch

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switch

- Pump Time Delay Relay

- Status Display Lights

#### Gas Train

- Manual Gas Shut-Off Valve(s)

- Combination Valves

- Low Gas Pressure Switch, Manual

- Firing Stages

2-Stage: Model 989B

3-Stage: Model 1259B

4-Stage: Models 1529B-2339B

- Fuel

Natural Gas

Propane Gas

- Design Certified - ANSI Z21.13/CSA 4.9

#### Burner

- Ultra-Low NOx: Less than 
20 PPM

#### Construction

- Indoor/Outdoor Construction

- Enclosed Front Controls

- CSA Low Lead Certified ≤ .25 Pb

#### Venting

- Vent Location

Top, Outdoor – Standard

Top, Indoor – Option D-20

Rear – Option D-14

- Vent Termination Cap

Outdoor D-11

Indoor, Horizontal D-15

Delta Limited models not approved for use in California

Indoor, Vertical (by others)

- Extractor – Optional

By others

Not required

#### Temperature Controls

B-6	Aquastat, 2-Stage (100-200ºF)

B-__	TempTracker Digital Controller, 2-Stage (Loose)

B-__	TempTracker Digital Controller, 4-Stage (Loose)

B-__	TempTracker Mod+ Hybrid (2-16 Boilers)

B-60	Stage Interface

#### Options

C-6	Ignition Module, Manual Reset

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 
1, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Start 
(See 2000.48)

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

For Metric information, see Catalog

#### Regulatory Agency Requirements

For Metric information, see Catalog

#### Delta Limited – Type H

Models 989B-2339B	Model

NOTE:
Pump location varies based on model selected

RATES OF FLOW AND PRESSURE DROPS

|  | 20°F ∆T |  | 30°F ∆T |  | ###### Min. Flow |  |  | ###### Max. Flow |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### Model | ###### GPM | ∆P (ft) | ###### GPM | ∆P (ft) | ###### GPM | ∆P (ft) | ###### ∆T | ###### GPM | ∆P (ft) | ###### ∆T |
| 989B | 84 | 5.6 | 56 | 2.5 | 42 | 1.5 | 40 | 132 | 14.0 | 13 |
| 1259B | 107 | 10.0 | 71 | 4.5 | 53 | 2.6 | 40 | 132 | 15.5 | 16 |
| 1529B | 130 | 16.0 | 86 | 7.1 | 65 | 4.1 | 40 | 132 | 16.5 | 20 |
| 1799B | N/A | N/A | 102 | 10.8 | 76 | 6.0 | 40 | 132 | 18.0 | 23 |
| 1999B | N/A | N/A | 113 | 14.0 | 85 | 8.1 | 40 | 132 | 19.5 | 26 |
| 2069B | N/A | N/A | 117 | 15.0 | 88 | 8.7 | 40 | 132 | 19.5 | 27 |
| 2339B | N/A | N/A | 132 | 21.0 | 99 | 12.0 | 40 | 132 | 21.0 | 30 |

Basis is 40°F ∆T for minimum flow, 132 GPM for maximum flow.

Raypak, Inc.  2151 Eastman Avenue, Oxnard, CA  93030  (805) 278-5300  Fax (800) 872-9725  www.raypak.com

SPECIFICATIONS

|  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH |  | Firing | A | H | K | W | Amp. | Shipping |
| Model | Input | Output | Stages | Width | NPT |  |  | Draw* | Wt. (Lbs.) |
| 989B | 990 | 832 | 2 | 57-1/8 | 2-1/2 | 10 | 16-13/16 | < 12 | 900 |
| 1259B | 1260 | 1058 | 3 | 68-1/2 | 2-1/2 | 12 | 20-9/16 | < 12 | 1010 |
| 1529B | 1530 | 1285 | 4 | 79-7/8 | 2-1/2 | 12 | 24-3/8 | < 12 | 1225 |
| 1799B | 1800 | 1512 | 4 | 91-1/8 | 2-1/2 | 14 | 28-1/8 | < 12 | 1350 |
| 1999B** | 1999 | 1679 | 4 | 102-1/2 | 2-1/2 | 14 | 31-15/16 | < 12 | 1450 |
| 2069B | 2070 | 1739 | 4 | 102-1/2 | 2-1/2 | 14 | 31-15/16 | < 12 | 1450 |
| 2339B | 2340 | 1966 | 4 | 113-7/8 | 2-1/2 | 16 | 35-11/16 | < 12 | 1520 |

* Pump not included

** Natural Gas Only

Dimensions are in inches.

Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

Recommended natural gas supply pressure is 7 – 10.5” WC. Recommended propane gas supply pressure is 
11 - 13” WC.